## ELEC LOAD SHEET
| PROJECT / BUILDING NAME : |  |  |  | F-F-052_HATTI KAAPI
| FED FROM : |  |  |  | EXISTING 63A MCCB ISOLATOR PANEL (FED FROM AIRPORT FEEDER)
| DISTRIBUTION BOARD / REF : |  |  |  | LPDB |  |  |  |  | DB AREA REFERENCE : |  |  | ELECTRICAL CLOSET @ UNDER COUNTER
| MAIN INCOMING CABLE : |  |  |  | 4 x 1C x 16 SQ.MM FRLS / LSZH CU. WIRES+ 1C x 16 SQ.MM ECC |  |  |  |  | DOCUMENT NO. :
MAIN INCOMER RATING | CIRCUIT ID | BREAKER TYPE | BREAKER RATING | WIRE SIZE (PH & N) | WIRE SIZE (EARTH) | EQUIP. TAG | CIRCUIT NAME / POINT REFERENCE | SOCKET RATING | NUMBER OF POINTS | CONN. LOAD / POINT | DIVERSITY TYPE | DIVERSITY FACTOR | R | Y | B | TOTAL CONN. LOAD | TOTAL DIVERSITY LOAD | REMARKS
(A) |  |  | (A) | (mm2) | (mm2) |  |  | (A) |  | (W) | [5 empty] | (kW) | (kW)
20A 30mA 4P RCBO | R1 | MCB | 10 | 2.5 | 1.5 | - | TRACK LIGHT (LT1) + INDICATIVE SIGNAGE | - | 10 | 320 | LTG | 1 | 0.32 |  |  | 0.32 | 0.32 | -
| Y1 | MCB | 20 | 4 | 2.5 | EQ-03 | DIGITAL DISPLAY | 13 | 3 | 200 | PWR | 1 |  | 0.6 |  | 0.6 | 0.6 | RADIAL CKT
| B1 | MCB | 20 | 4 | 2.5 | HK - 02 | HATTI KAPPI TEA / COFFEE VENDING MACHINE | 20 | 1 | 2000 | PWR | 0.8 |  |  | 2 | 2 | 1.6 | -
| R2 | MCB | 20 | 4 | 2.5 | HK - 04 | SANDWICH GRILLER | 16 | 1 | 2000 | PWR | 0.8 | 2 |  |  | 2 | 1.6 | -
| Y2 | MCB | 16 | 2.5 | 1.5 | HK - 05 | MICROWAVE OVEN | 16 | 1 | 1550 | PWR | 0.8 |  | 1.55 |  | 1.55 | 1.24 | -
| B2 | MCB | 16 | 2.5 | 1.5 | HK - 06 | TWO DOOR WORK TOP CHILLER ( COMPRESSOR ON RHS ) | 13 | 1 | 375 | PWR | 0.8 |  |  | 0.375 | 0.375 | 0.3 | -
| R3 | MCB | 20 | 4 | 2.5 | SP-01 | 13A SPARE | 13 | 3 | 100 | PWR | 0.5 | 0.3 |  |  | 0.3 | 0.15 | RADIAL CKT
| Y3 | MCB | 16 | 2.5 | 1.5 | HK - 08 | COLD DISPLAY COUNTER | 13 | 1 | 1000 | PWR | 0.8 |  | 1 |  | 1 | 0.8 | -
| B3 | MCB | 20 | 4 | 2.5 | SP-03 | 20A SPARE | 20 | 1 | 500 | PWR | 0.5 |  |  | 0.5 | 0.5 | 0.25 | -
| R4 | MCB | 20 | 4 | 2.5 | - | UPS (UPS DB) | - | 1 | 900 | UPS | 1 | 0.9 |  |  | 0.9 | 0.9 | -
| Y4 | MCB | 16 | 2.5 | 1.5 | EQ-01 | BOOSTER PUMP | 13 | 1 | 400 | PWR | 0.5 |  | 0.4 |  | 0.4 | 0.2 | -
| B4 | MCB | 16 | 2.5 | 1.5 | SP-02 | 16A SPARE | 16 | 1 | 200 | PWR | 1 |  |  | 0.2 | 0.2 | 0.2 | -
40A 30mA 4P RCBO | RYB5 | RCBO | 40 | 10 | 10 | - | CHAI POINT DISTRIBUTION BOARD | - | 1 | 37690 | PWR |  | 12.5633 | 12.5633 | 12.5633 | 37.69 | 19.76 | -
.
[12 empty] | LPDB | 16.0833 | 16.1133 | 15.6383 | 47.835 | 27.92
[13 empty] | TCL - R | TCL - Y | TCL - B | TCL | TDL
ABBREVIATIONS : PWR - POWER, LTG - LIGHTING, UPS - UNINTERRUPTIBLE POWER SUPPLY, A - AMPS, W - WATTS, kW - KILOWATT, 1R - ONE RUN, 4C - FOUR CORE, 2C - TWO CORE, CU. - COPPER, ECC - EARTH CONTINUITY CONDUCTOR, CONN. - CONNECTED
| DISTRIBUTION BOARD / REF : |  |  |  | UPS DB |  |  |  |  | DB AREA REFERENCE : |  |  | ELECTRICAL CLOSET @ UNDER COUNTER
| MAIN INCOMING CABLE : |  |  |  | 2 x 1C x 4 SQ.MM FRLS/LSZH CU. CABLE + 1C x 4 SQ.MM ECC |  |  |  |  | DOCUMENT NO. :
MAIN INCOMER RATING | CIRCUIT ID | BREAKER TYPE | BREAKER RATING | WIRE SIZE (PH & N) | WIRE SIZE (EARTH) | EQUIP. CODE | CIRCUIT NAME / POINT REFERENCE | SOCKET RATING | NUMBER OF POINTS | CONN. LOAD / POINT | DIVERSITY TYPE | DIVERSITY FACTOR | R | Y | B | TOTAL CONN. LOAD | TOTAL DIVERSITY LOAD | REMARKS
(A) |  |  | (A) | (mm2) | (mm2) |  |  | (A) |  | (W) | [5 empty] | (kW) | (kW)
20A 30mA 2P RCBO | C1 | MCB | 20 | 4 | 2.5 | HK - 07 | POS WITH PRINTER | 13A | 4 | 100 | PWR | 1 | 0.4 |  |  | 0.4 | 0.4 | RADIAL CKT
| C2 | MCB | 16 | 2.5 | 1.5 | EQ-02 | DVR | 13A | 1 | 300 | PWR | 1 | 0.3 |  |  | 0.3 | 0.3 | -
| C3 | MCB | 16 | 2.5 | 1.5 | - | SPARE | - | 1 | 200 | PWR | 1 | 0.2 |  |  | 0.2 | 0.2 | -
| C4 | - | - | - | - | - | SPACE | - |  |  |  |  | 0 |  |  | 0 | 0 | -
.
[12 empty] | UPS DB | 0.9 | 0 | 0 | 0.9 | 0.9
[13 empty] | TCL - R | TCL - Y | TCL - B | TCL | TDL
ABBREVIATIONS : PWR - POWER, LTG - LIGHTING, UPS - UNINTERRUPTIBLE POWER SUPPLY, A - AMPS, W - WATTS, kW - KILOWATT, 1R - ONE RUN, 4C - FOUR CORE, 2C - TWO CORE, CU. - COPPER, ECC - EARTH CONTINUITY CONDUCTOR, CONN. - CONNECTED
[7 empty] | TOTAL CONNECTED LOAD | 47.835 | LPDB | + | UPS DB | TCL (kW)
[7 empty] | TOTAL DEMAND LOAD | 27.92 | LPDB | + | UPS DB | TDL (kW)
[7 empty] | AVERAGE DIVERSITY FACTOR | 58.37% | LPDB | + | UPS DB | (%)