## GIAN'S
FIRE FIGHTING WORK BOQ
GIANI'S
S. No. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps, U bolt and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings , breakages and making good the same. ( Final Quantity Measure as per site after working )
1.1 | 25 mm dia | Mtr. | 7 |  | 0
1.2 | 32 mm dia | Mtr. | 0 |  | 0
1.3 | 40 mm dia | Mtr. | 0 |  | 0
1.4 | 50 mm dia | Mtr. | 0 |  | 0
1.5 | 65 mm dia | Mtr. | 0 |  | 0
1.6 | 80 mm dia | Mtr. | 0 |  | 0
1.7 | 100 mm dia | Mtr. | 0 |  | 0
1.8 | 150 mm dia | Mtr. | 0 |  | 0
1.9 | 200 mm dia, 6.0 mm thick | Mtr. | 0 |  | 0
2 | Supply, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 and 1239 for hydrent and sprinkler underground rings including all accessories such as screwed/ welded flanges, tees, reducers etc. Conforming to IS : 1239/3589 complete including , welding, jointing with compressed asbestos gaskets, nuts, bolts etc. as required. with cleaning, wrapping and coating of the pipe with 4 mm thick tar based plymaric corrosion protection tape or equivalent including applying uniform coat of cold pipekot primer as per IS; 10221 for protection against corrsion suitable for all kind of soil at 1.0 M depth including excavation and making good the same as required at site . ( Final Quantity Measure as per site after working )
2.1 | 80 mm dia | Mtr. | 0 |  | 0
2.2 | 100 mm dia | Mtr. | 0 |  | 0
2.3 | 150 mm dia | Mtr. | 0 |  | 0
3 | Supply, installation, testing and commissioning of Brass ball valves of following sizes as required.
3.1 | 25 mm dia. | Each | 1 |  | 0
3.2 | 32 mm dia. | Each | 0 |  | 0
3.3 | 40 mm dia. | Each | 0 |  | 0
3.4 | 50 mm dia | Each | 0 |  | 0
3.5 | 65mm dia. | Each | 0 |  | 0
4 | Supply, fixing, testing & commissioning of 15 mm dia size ,quartzoid bulb sprinkler heads suitable for 68 degree centigrade rating of the following type :
4.1 | Pendant type | Each | 2 |  | 0
4.2 | Upright type | Each | 0
4.3 | Side wall type | Each | 0 |  | 0
5 | Supply & Fixing ISI marked ( IS : 15683 ) Portable Fire Exitnguisher, ABC type,finished externally with red enamel paint, complete in all respects including initial fill and wall suspension of following capacity.
5.1 | 6 kg | Each | 1 |  | 0
6 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, Carbon‐dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307‐1966 filled to a filling ratio of not more than 0.667and wall suspension bracket. Capacity 5 Kg. | Each | 1 |  | 0
7 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, k type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill. Capacity 6kg | Each | 0
8 | Supply and fixing M.S. structural work fabricated from standard sections i.e. rounds, solid angles, slotted angles, channels including cutting to size, drilling, welding, fixing and welding to insert plates in RCC structural members as directed by Engineer-in-charge including cutting and making good the walls and floors (for hangers, supports, clamps, etc.) | Kg | 0 |  | 0
9 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required.
9.1 | 700 MM LONG | Each | 0 |  | 0
| TOTAL COST IN Rs. |  |  |  | 0
VARIATION COST +-10 TO 20%
APPROVED MAKES
A | FIRE pump
Mather & Platt ( Wilo ), Kirloskar,LUBI, Grundfos,XYLEM
C | MS / GI pipes
Prakash Surya , TT Swastik , Jindal (Hisar ), Tata
D | Pipe Coat Material
Pypkote, Makphalt, Safex, mlote
E | Sluice / Butterfly / Non return / Ball valves
Audco , Advance , Zoloto , Kirloskar , Intervalve, Leader, Cim
F | Fire hydrant valves / Short branch pipe / FB Withdrawl & Inlet
Newage, Ceasefire, Vijay, Minimax, Eversafe , Peter autokit , Padmini
G | Fire hose pipes / First aid fire hose reel / Fireman's Axe
Newage, Ceasefire, Jayshree , Ushafire, Safex, Eversafe, Jyoti
H | Sprinkler heads
Tyco, Eversafe, Reliable, Spraysafe, Viking
I | Fire Extinguishers
Cease fire, Safex, Minimax, Newage, Peterautokit, Eversafe, Ansul

## Sheet2 (hidden)
|  | B.F | G.F | 1ST FLOOR | 2ND FLOOR | 3RD FLOOR | 4TH FLOOR | T
| WALL SPLNKR | 3 | [5 empty] | 3
| SPLNKR | 43 | [5 empty] | 43
0
| 25 | 83 | [5 empty] | 83
| 32 | 27 | [5 empty] | 27
| 40 | 15 | [5 empty] | 15
| 50 | 11 | [5 empty] | 11
| 65 | 15 | [5 empty] | 15
| 80 | 4 | [5 empty] | 4
| 100 | [6 empty] | 0
| 150 | [6 empty] | 0
| 15 | 3.5 | 52.5
| 165 | 50.3049
|  | PUMP | 10
10
10
EXTERNAL