## GIANI'S
UNA FOOD COURT
DRAINAGE & WATER SUPPLY WORK BOQ
OUTLET-2 GIAN'S
S. No. | Description | Unit | Qty. | Rate | Amount | Make
A | WATER SUPPLY PIPING
1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes SDR 11, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. (Concealed work including cutting chases and making good the walls etc.,) Pressure Testing (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  |  | Astral / Ashirwad /supreme / Prince or Approved Equivalent
1.1 | 15 mm Dia | R.mt | 0
1.2 | 20 mm Dia | R.mt | 17
1.3 | 25 mm Dia | R.mt | 7
1.4 | 32mm Dia | R.mt | 0
2 | Providing & fixing gun metal lever operated ball valve. Tested to a pressure of 15 Kg / Sqcm. Including flanges/union, nuts, bolts, washer etc. Complete as required. |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
2.1 | 20mm Dia | Nos. | 0
2.2 | 25mm Dia | Nos. | 2
2.3 | 32mm Dia | Nos. | 0
2.4 | 40mm Dia | Nos. | 0
3 | Providing, fixing, testing and commissioning of NRV with forged brass body, brass diaphram and SS seal in water supply pipes. Complete as required. |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
3.1 | 25mm Dia | Nos. | 1
4 | Providing, fixing, testing and commissioning of Y STRAINER FLANGED END EPOXY COATED WITH SS SCREEN (CR16B) |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
4.1 | 25mm Dia | Nos. | 1
5 | Providing and fixing of brass multijet water meters with magnetic transmision of IS-779:1994 including with rubber gasket, flanges/ unions, nuts, bolts, washers, etc. complete as required. Make : Kranti
5.1 | 25 mm Dia incoming line | Nos. | 1
5.2 | 32 mm Dia incoming line | Nos. | 0
5.3 | 40 mm Dia incoming line | Nos. | 0
6 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  |  |  |  | AO Smith or Approved Equivalent
6.1 | 3 L Capacity- | Nos. | 1
6.2 | 20 L Capacity | Nos. | 0
6.3 | 25 L Capacity- | Nos. | 0
7 | SITC of Eco smart RO 50 LPH Capacity with all required accessories | Nos | 0 |  |  | Iron Exchange or Approved Equivalent
8 | SITC of grease trap -model NGT-14 Capacity -25.5 lit ( 28 LPM) with all required accessories( SIZE:- | Nos | 1 |  |  | NUGREEN, Aco or Approved Equivalent
9 | SITC of grease trap -model NGT-30 Capacity -47.5 lit ( 57 LPM) with all required accessories( SIZE:- | Nos | 0 |  |  | NUGREEN, Aco or Approved Equivalent
B | DRAINAGE
1 | Providing and fixing Upvc SWR pipes ( Class B Heavy Type) including all fittings (plain or door) e.g. bends, junction, cowls, offsets, access pieces, jointing with rubber ring/solvent cement joints,jali,clamps including cutting chase or holes in walls and floors and making good where required.( Inside the building) |  |  |  |  | ASTRAL/PRINCE/ SUPREME
1.1 | 50mm Dia | R.mt | 3
1.2 | 75mm Dia | R.mt | 1
1.3 | 110 mm Dia | R.mt | 5
1.4 | 150 mm Dia | R.mt | 0
2 | Providing & fixing in position pipe trap of self cleaning design of following sizes for the embedded areas. Making proper connection with , cutting chase / hole in floors /slabs and bringing the same in proper condition in cement concrete 1:2:4 mix complete as required. including cost of cutting and making good the walls and floors where required. Make : |  |  |  |  | ASTRAL/PRINCE/ SUPREME
2.1 | P-trap 110 mm dia | Each | 0
2.2 | Multi trap 110 mm dia with square grating (Outlet 75MM dia) | Each | 0
2.3 | Floor trap 110 mm dia with grating(Outlet 75MM dia) | Each | 0
2.4 | Nahani trap 110 mm dia with grating(Outlet 75MM dia) | Each | 1
C | SANITARY AND C. P. FITTINGS & FIXTURES
Only installation, testing and commissioning of sanitary and C.P. fittings
1.1 | Providing and Fixing of S.S. sink without drain board over all size 450Wx700Dx900H mm Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 1 |  |  | NIRALI OR EQUIVALENT
1.2 | Providing and Fixing of RO S.S. sink without drain board over all size 600Wx700Dx850H mm +200 High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 0 |  |  | NIRALI OR EQUIVALENT
1.3 | Providing and Fixing of S.S. sink without drain board over all size 450Wx450Dx850H mm High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 1 |  |  | NIRALI OR EQUIVALENT
1.4 | Providing and Fixing of Three Bowl S.S. sink without drain board over all size 1500Wx700Dx850H mm +100 High Single bowl size:- with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos | 0 |  |  | NIRALI OR EQUIVALENT
1.2 | Providing and Fixing C.P. brass wall mounted/ table top sink mixer with swinging spout, wall mounted type complete as required. | Nos | 2 |  |  | NIRALI OR EQUIVALENT
1.4 | Angle Cock with PVC pipe connection upto sink/Geyser /RO connection | Nos | 6 |  |  | JAQUAR OR EQUIVALENT
D | S.S. GRATING
SITC of , testing and commissioning of S.S.Gratings
1 | Making chamber in brick work including internal tiling etc for S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 2
GRAND - TOTAL A , B, C AND D