## SUMMARY
CARL'S JUNIOR @ T3, LUCKNOW AIRPORT
HVAC BOQ SUMMARY
Sr.No | Description | Total Amount
4 | SHEET METAL WORKS: | 0
5 | THERMAL & ACOUSTIC INSULATION: | 0
6 | ELECTRICAL WORKS: | 0
SUB - TOTAL WITHOUT TAX
CGST @ 9%
SGST @ 9%
Other taxes if applicable
TOTAL WITH TAX

## HVAC
CARL'S JUNIOR @ T3, LUCKNOW AIRPORT
HVAC BOQ
Sr. No. | Description Items | Unit | Qty | Supply Rate | Installation Rate | Total Amount
Sr.No. | Item Description
4 | SHEET METAL WORKS:
4.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 10 |  |  | 0
d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 110 |  |  | 0
4.2 | EXTRUDED ALUMINIUM CEILING GRILLES
Supply, Installation, Testing and Balancing of Powder coated aluminium supply air grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square/rectangular/Linear). The grilles shall be with 15/30/45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
Make: Cosmos, Air Master & System Air
| Linear / Square / Rectangular Grille | Sq.mtr | 1 |  |  | 0
| Curve Grille | Sq.mtr | 1 |  |  | 0
4.3 | DOOR TRANSFER GRILLE
SITC of Aluminium extruded powder coated Door transfer grills.
| Door transfer grille (Back to Back) | Sq.mtr | 0.5 |  |  | 0
Make: Cosmos, Air Master & System Air
4.4 | MULTI LEAF VOLUME CONTROL DAMPER
| SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 1
Make: Cosmos, Air Master & System Air
4.5 | OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 1 |  |  | 0
4.6 | CANVAS CONNECTION
SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
a | For AHU | No | 1 |  |  | 0
b | For TFA | No | 1 |  |  | 0
4.7 | CURTAIN TYPE FIRE DAMPER
SITC of fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 / 225°F, etc; as per the approved shop drawings and specifications.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Bare fire dampers | Sq.mtr | 1
b | Fusible link as per specification UL 555 | No | 1
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
SUB-TOTAL
5 | THERMAL & ACOUSTIC INSULATION:
5.1 | THERMAL INSULATION
| Supply & fixing of Thermal insulation for supply air duct using 13mm thick class " O " Closed cell nitrile rubber with anti-microbial coating on it. Insulation shall have Thermal conductivity of 0.033 W/(m.K) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape. The duct shall be stick with recommended adhesive. | Sq.mtr | 35
Make: Armaflex & K-flex
5.2 | ACOUSTIC INSULATION
| Supply & fixing acoustic insulation for ducting using Class "1" closed cell elastomeric insulation of 10mm thick Nitrile rubber insulation adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. Material shall be processed Nitrile Rubber foam with anti-microbial protection. Insulation shall have thermal conductivity of 0.047 W/(m.K) and density of 140 - 180 kg/m³. | Sq.mtr | 15
Make: Armaflex & K-flex
5.3 | THERMAL INSULATION FOR KITCHEN EXHAUST DUCTS
| SITC of 50mm thick Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density : 32 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade. | Sq.mtr | 40
Make: Rockwool / UP Twiga
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.
SUB-TOTAL
6 | ELECTRICAL WORKS:
6.2 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
a | Suitable Power Cable:
| Suitable for 900 CFM AHU, DOL Starter Panel | Rmt | 10 |  |  | 0
| Suitable for 600 CFM TFA, DOL Starter Panel | Rmt | 10 |  |  | 0
| Suitable for 4300 CFM Dry Scrubber, 1 ph | Rmt | 10 |  |  | 0
b | Earthing:
| 8 SWG | Rmt | 40 |  |  | 0
6.3 | BTU METER
Supply,fixing and testing of inline Btu meter for the flow rate & temperature measurement consisting mainly of following 3 parts
a) Ultrasonic Flow Meter
b) Matched pair of temp sensor
c) Flowcell Sensor
c) BTU Meter - 4 - 20mA DC from flowmeter
Insertion type flowmeter shall be suitable for chilled water application for temp. Ranging from 0 to 50 deg C. Power supply shall be 240V AC (+/-) 15 %. Display shall have 16 characters LCD display with Back light, flow rate, Velocity, totaliser etc. Output shall be BMS Modbus compatible & shall have keypad lockout security option. It also should be able to show various units such as gallons, ft^3, lbs, liters, m^3, kg etc
Make: Honeywell / Danfoss / Siemens
a | Dia 32 mm | No. | 1
6.4 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
a | Suitable for 900 CFM AHU, DOL Starter Panel | Nos. | 2 |  |  | 0
b | Suitable for 600 CFM TFA, DOL Starter Panel | Nos. | 2 |  |  | 0
6.5 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm wide | Rmt | 20 |  |  | 0
SUB-TOTAL
GRAND TOTAL