## HVAC (3)
- | - | - | - | -
1 | SPLIT UNITS - DUCTABLE UNITS & HIWALL UNITS | - | - | -
1.1 | Removal of existing 8.5TR Ductable Indoor Units & storing them in a good condition | - | - | -
a | 8.5TR Ductable Unit | Nos | 8 | 0
- | - | - | - | -
1.2 | Re-Installation of existing 8.5TR Ductable Units. Vaccumizing, pressure testing, gas charging & commissioning of the same | - | - | -
a | 8.5TR Ductable Unit | Nos | 8 | 0
- | - | - | - | -
1.3 | Gas Required for commissioning | Kgs | 50 | 0
- | - | - | - | -
1.4 | Indoor Stands for 8.5TR Ductable Unit | Nos | 8 | 0
- | - | - | - | -
1.5 | Epoxy paint, Enamel paint & modification if required for existing outdoor unit stand | Nos | 8 | 0
- | - | - | - | -
1.6 | 1.5TR Hiwall Split Unit ( 3 Star ) | Nos | 0 | -
- | - | - | - | -
2 | REFRIGERANT COPPER PIPING FOR DUCTABLE UNITS | - | - | -
2.1 | Supply, installation, testing & commissioning of refrigerant copper piping connected between odu unit & IDU units covered with19 mm thick XLPE insulation. | - | - | -
a | Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Ductable Unit | Rmt | 10 | -
b | Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Hiwall Unit | Rmt | 2 | -
- | - | - | - | -
2.2 | Communication Cable if required. Existing cable will be used. 3 Core x 2.5 Sqm Shielded Copper Cable in PVC Conduits(ODU TO IDU) | Rmt | 0 | -
- | - | - | - | -
- | - | - | - | -
3 | FAN | - | - | -
3.1 | Supply, installation, commissioning & testing of Inline fans (Exhaust & Fresh Air Fan) | - | - | -
a | Capacity: 400 cfm @ 15 mm WC static pressure- Fresh Air Fan | Nos | RO | -
b | Capacity: 500 cfm @ 15 mm WC static pressure - Fresh Air Fan | Nos | RO | -
c | Capacity: 500 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO | -
d | Capacity: 700 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO | -
- | - | - | - | -
4 | CONDENSATE DRAIN PIPING | - | - | -
- | Supply, installation, testing & Commissioning of PVC drain pipe of following sizes with 9mm thick XLPE insulation. | - | - | -
a | 50mm dia With 9mm XLP insulation | Rmt | 35 | -
b | 40mm dia With 9mm XLP insulation | Rmt | 12 | -
c | 32mm dia With 9mm XLP insulation | Rmt | 15 | -
d | 25mm dia With 9mm XLP insulation | Rmt | RO | -
- | - | - | - | -
5 | DUCTWORK & ACCESSORIES | - | - | -
5.1 | Rectangular Ducting | - | - | -
- | 24G -Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 265 | -
- | 22G - Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 125 | -
- | - | - | - | -
5.2 | Supply, Installation, testing & commissioning of factory built Manual Volume Control Dampers | Sq.m | 2 | -
- | - | - | - | -
5.3 | Supply, Installation, testing & commissioning of factory built Collar Volume Control Dampers | Sq.m | 11 | -
- | - | - | - | -
5.4 | Supply, Installation, testing & commissioning of factory built Fire Control Dampers | Sq.m | RO | -
- | - | - | - | -
5.5 | Fusible Link for Fire Control Dampers | Nos | RO | -
- | - | - | - | -
5.6 | Supply, Installation, testing & commissioning of factory built AL Birdscreen with louvers | Sq.m | 1 | -
- | - | - | - | -
5.7 | Insulated Plenum boxes 200 x 300 x 650 | Nos | 80 | -
- | - | - | - | -
5.8 | SITC and balancing of grills and deffusers | - | - | -
5.8.1 | 3 slot grills for supply air with hit and miss dampers complete with air patern controller. | RM | 70 | -
5.8.2 | 3 slot grills for return air without dampers complete with air patern controller. | RM | RO | -
5.8.3 | Linear Air Grilles with Al. VCD - Linear Fixed Bar Grilles, Horizontal Fixed with removable cores, core styles 1/2/3 way with opposed Blade aluminium Bars, Normal Blade (5 mm nominal thickness) Grille height 16 mm, blade pitch 12.5 mm. 150mm wide linear grilles without dampers | Sq.m | 0 | -
5.8.4 | Linear Air Grilles without VCD - Linear Fixed Bar Grilles for Return Air 150mm wide linear grilles without dampers | Sq.m | 12 | -
- | - | - | - | -
5.8 | DIFFUSER | - | - | -
a | Supply Air Diffusers with Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction VCD Black Anodized | Nos | RO | -
b | Return Air Diffusers without Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction. | Nos | RO | -
- | - | - | - | -
5.9 | Supply and installation of return air Disc valve (TOILET EXHAUST & FRESH AIR) | - | - | -
- | 150dia | Nos | RO | -
- | - | - | - | -
5.10 | Supply Installation testing and comissioning of insulated flexible duct of given sizes. Make Twiga or equal | - | - | -
- | - | - | - | -
a | Dia 200 | Rmt | 60 | -
- | - | - | - | -
5.11 | GI Rings for Flexible Connections | - | - | -
a | 200 Dia | Nos | 160 | -
b | 300 Dia | Nos | RO | -
- | - | - | - | -
5.12 | Return air Z Piece ( 300 x 300 x 900 ) with Insulation | Nos | RO | -
- | - | - | - | -
6 | INSULATIONS-HVAC | - | - | -
6.1 | Thermal duct insulation : | - | - | -
a | 13mm thick Al.Faced XLPE insulation ('Aerofoam' or approved equivalent) | Sq.m | 350 | -
- | - | - | - | -
6.2 | Duct Accoustic Insulation | - | - | -
a | Acoustic insulation of Ducts - Physically crosslinked Open cell polyolefin foam with factory applied reinforced aluminium foil having density of 25kg/m3 and meeting the Class 0 requirements of Fire safety as per BS 476 Part 6 & 7.The material shall be antifungal in nature and tested to ASTM G21 standard The NRC of 15mm thick material would be 0.4 when tested as per ISO 354 standard. 25mm ( Self Adhesive Only ) Approved Makes - Aerofoam / Thermobreak or equal | Sq.m | 125 | -
- | - | - | - | -
6.3 | Under deck Insulastion | - | - | -
a | Insulation material shall be Closed Cell Elastomeric Armaflex Nitrile Rubber, Density of Material shall be between 45 + 5 kg/m3, Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.035 W/mK at mean temperature of 0C,• The insulation shall have fire performance such that it passes Class 1 as per BS476 Part 7 for surface spread of flame and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire category, Material should be FM (Factory Mutual), USA approved, Moisture Diffusion Resistance Factor ‘µ’ value should be minimum 7000For Concrete Slab: 25 mm thick sheet is used & For Corrugated or metal ceiling: 32 mm thick sheet | Sq.m. | 330 | -
- | - | - | - | -
7 | Scaffolding for Ducting work at Double height area. | Lot | 1 | -
- | - | - | - | -
- | - | - | - | -
- | - | - | - | -
- | - | - | - | -
- | - | - | - | -
- | Taxes Extra as applicable | - | - | -

## HVAC (2)
a | 8.5TR Ductable Unit | Nos | 8 | 0 |  | 0 | 0 | OPTIONAL COST
a | 8.5TR Ductable Unit | Nos | 8 | 0 |  | 0 | 0
1.3 | Gas Required for commissioning | Kgs | 50 | 0 |  | 0 | 0
1.4 | Indoor Stands for 8.5TR Ductable Unit | Nos | 8 | 0 |  | 0 | 0
1.5 | Epoxy paint, Enamel paint & modification if required for existing outdoor unit stand | Nos | 8 | 0 |  | 0 | 0
1.6 | 1.5TR Hiwall Split Unit ( 3 Star ) | Nos | 0 |  |  | 0 | 0
2 | REFRIGERANT COPPER PIPING FOR DUCTABLE UNITS | Nos | 0 |  |  | 0 | 0
2.1 | Supply, installation, testing & commissioning of refrigerant copper piping connected between odu unit & IDU units covered with19 mm thick XLPE insulation. | Nos | 1
a | Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Ductable Unit | Rmt | 10 |  |  |  | 0
b | Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Hiwall Unit | Rmt | 2 |  |  |  | 0
2.2 | Communication Cable if required. Existing cable will be used. 3 Core x 2.5 Sqm Shielded Copper Cable in PVC Conduits(ODU TO IDU) | Rmt | 0 |  |  |  | 0
3 | FAN | Nos | 1 |  |  |  | 0
3.1 | Supply, installation, commissioning & testing of Inline fans (Exhaust & Fresh Air Fan) | Nos | 0
a | Capacity: 400 cfm @ 15 mm WC static pressure- Fresh Air Fan | Nos | RO
b | Capacity: 500 cfm @ 15 mm WC static pressure - Fresh Air Fan | Nos | RO
c | Capacity: 500 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO
d | Capacity: 700 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO
4 | CONDENSATE DRAIN PIPING
Supply, installation, testing & Commissioning of PVC drain pipe of following sizes with 9mm thick XLPE insulation.
a | 50mm dia With 9mm XLP insulation | Rmt | 35 |  |  |  | 0
b | 40mm dia With 9mm XLP insulation | Rmt | 12 |  |  |  | 0
c | 32mm dia With 9mm XLP insulation | Rmt | 15 |  |  |  | 0
d | 25mm dia With 9mm XLP insulation | Rmt | RO
5 | DUCTWORK & ACCESSORIES
5.1 | Rectangular Ducting
| 24G -Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 265 |  |  |  | 0
| 22G - Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 125 |  |  |  | 0
5.2 | Supply, Installation, testing & commissioning of factory built Manual Volume Control Dampers | Sq.m | 2 |  |  |  | 0
5.3 | Supply, Installation, testing & commissioning of factory built Collar Volume Control Dampers | Sq.m | 11 |  |  |  | 0
5.4 | Supply, Installation, testing & commissioning of factory built Fire Control Dampers | Sq.m | RO
5.5 | Fusible Link for Fire Control Dampers | Nos | RO
5.6 | Supply, Installation, testing & commissioning of factory built AL Birdscreen with louvers | Sq.m | 1 |  |  |  | 0
5.7 | Insulated Plenum boxes 200 x 300 x 650 | Nos | 80 |  |  |  | 0
5.8 | SITC and balancing of grills and deffusers
5.8.1 | 3 slot grills for supply air with hit and miss dampers complete with air patern controller. | RM | 70 |  |  |  | 0
5.8.2 | 3 slot grills for return air without dampers complete with air patern controller. | RM | RO
5.8.3 | Linear Air Grilles with Al. VCD - Linear Fixed Bar Grilles, Horizontal Fixed with removable cores, core styles 1/2/3 way with opposed Blade aluminium Bars, Normal Blade (5 mm nominal thickness) Grille height 16 mm, blade pitch 12.5 mm. 150mm wide linear grilles without dampers | Sq.m | 0 |  |  |  | 0
5.8.4 | Linear Air Grilles without VCD - Linear Fixed Bar Grilles for Return Air 150mm wide linear grilles without dampers | Sq.m | 12 |  |  |  | 0
5.8 | DIFFUSER
a | Supply Air Diffusers with Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction VCD Black Anodized | Nos | RO
b | Return Air Diffusers without Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction. | Nos | RO
5.9 | Supply and installation of return air Disc valve (TOILET EXHAUST & FRESH AIR)
| 150dia | Nos | RO
5.10 | Supply Installation testing and comissioning of insulated flexible duct of given sizes. Make Twiga or equal
0
a | Dia 200 | Rmt | 60 |  |  |  | 0
0
5.11 | GI Rings for Flexible Connections
a | 200 Dia | Nos | 160 |  |  |  | 0
b | 300 Dia | Nos | RO
5.12 | Return air Z Piece ( 300 x 300 x 900 ) with Insulation | Nos | RO
6 | INSULATIONS-HVAC
6.1 | Thermal duct insulation :
a | 13mm thick Al.Faced XLPE insulation ('Aerofoam' or approved equivalent) | Sq.m | 350 |  |  |  | 0
6.2 | Duct Accoustic Insulation
a | Acoustic insulation of Ducts - Physically crosslinked Open cell polyolefin foam with factory applied reinforced aluminium foil having density of 25kg/m3 and meeting the Class 0 requirements of Fire safety as per BS 476 Part 6 & 7.The material shall be antifungal in nature and tested to ASTM G21 standard The NRC of 15mm thick material would be 0.4 when tested as per ISO 354 standard. 25mm ( Self Adhesive Only ) Approved Makes - Aerofoam / Thermobreak or equal | Sq.m | 125 |  |  |  | 0
6.3 | Under deck Insulastion
a | Insulation material shall be Closed Cell Elastomeric Armaflex Nitrile Rubber, Density of Material shall be between 45 + 5 kg/m3, Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.035 W/mK at mean temperature of 0C,• The insulation shall have fire performance such that it passes Class 1 as per BS476 Part 7 for surface spread of flame and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire category, Material should be FM (Factory Mutual), USA approved, Moisture Diffusion Resistance Factor ‘µ’ value should be minimum 7000For Concrete Slab: 25 mm thick sheet is used & For Corrugated or metal ceiling: 32 mm thick sheet | Sq.m. | 330 |  |  |  | 0
7 | Scaffolding for Ducting work at Double height area. | Lot | 1 |  |  |  | 0
[5 empty] | Sub Total | 0 | 0
[5 empty] | Total |  | 0
Taxes Extra as applicable

## HVAC
PROJECT: | BLUESEA BANQUETS |  |  |  |  | 18.06.2024
ARCHITECT: ABM ARCHITECTS |  | BOQ FOR HVAC WORKS
BILL OF QUANTITIES |  |  |  | RATE |  | AMOUNT
SR. NO. | PARTICULARS | UNIT | QTY. | Supply | Installation | Supply | Installation
1 | SPLIT UNITS - DUCTABLE UNITS & HIWALL UNITS
1.1 | Removal of existing 8.5TR Ductable Indoor Units & storing them in a good condition
a | 8.5TR Ductable Unit | Nos | 8 | 0 |  | 0 | 0 | OPTIONAL COST
1.2 | Re-Installation of existing 8.5TR Ductable Units. Vaccumizing, pressure testing, gas charging & commissioning of the same
a | 8.5TR Ductable Unit | Nos | 8 | 0 |  | 0 | 0
1.3 | Gas Required for commissioning | Kgs | 50 | 0 |  | 0 | 0
1.4 | Indoor Stands for 8.5TR Ductable Unit | Nos | 8 | 0 |  | 0 | 0
1.5 | Epoxy paint, Enamel paint & modification if required for existing outdoor unit stand | Nos | 8 | 0 |  | 0 | 0
1.6 | 1.5TR Hiwall Split Unit ( 3 Star ) | Nos | 0 |  |  | 0 | 0
2 | REFRIGERANT COPPER PIPING FOR DUCTABLE UNITS
2.1 | Supply, installation, testing & commissioning of refrigerant copper piping connected between odu unit & IDU units covered with19 mm thick XLPE insulation.
a | Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Ductable Unit | Rmt | 10 |  |  |  | 0
b | Liquid& Gas Cu Piping with 19mm Al Faced XLPE insulation for Hiwall Unit | Rmt | 2 |  |  |  | 0
2.2 | Communication Cable if required. Existing cable will be used. 3 Core x 2.5 Sqm Shielded Copper Cable in PVC Conduits(ODU TO IDU) | Rmt | 0 |  |  |  | 0
3 | FAN
3.1 | Supply, installation, commissioning & testing of Inline fans (Exhaust & Fresh Air Fan)
a | Capacity: 400 cfm @ 15 mm WC static pressure- Fresh Air Fan | Nos | RO
b | Capacity: 500 cfm @ 15 mm WC static pressure - Fresh Air Fan | Nos | RO
c | Capacity: 500 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO
d | Capacity: 700 cfm @ 15 mm WC static pressure- Exhaust Air Fan | Nos | RO
4 | CONDENSATE DRAIN PIPING
Supply, installation, testing & Commissioning of PVC drain pipe of following sizes with 9mm thick XLPE insulation.
a | 50mm dia With 9mm XLP insulation | Rmt | 35 |  |  |  | 0
b | 40mm dia With 9mm XLP insulation | Rmt | 12 |  |  |  | 0
c | 32mm dia With 9mm XLP insulation | Rmt | 15 |  |  |  | 0
d | 25mm dia With 9mm XLP insulation | Rmt | RO
5 | DUCTWORK & ACCESSORIES
5.1 | Rectangular Ducting
| 24G -Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 265 |  |  |  | 0
| 22G - Ducting Factory Fabricated as per IS standards with angle Iron Flanges. (Supply and Installation of GI sheet metal duct, heavy duty GI angle / rod / wire supports, adjustable volume control Splitter dampers, guide vanes with necessary flexible connections, etc.) | Sq.m | 125 |  |  |  | 0
5.2 | Supply, Installation, testing & commissioning of factory built Manual Volume Control Dampers | Sq.m | 2 |  |  |  | 0
5.3 | Supply, Installation, testing & commissioning of factory built Collar Volume Control Dampers | Sq.m | 11 |  |  |  | 0
5.4 | Supply, Installation, testing & commissioning of factory built Fire Control Dampers | Sq.m | RO
5.5 | Fusible Link for Fire Control Dampers | Nos | RO
5.6 | Supply, Installation, testing & commissioning of factory built AL Birdscreen with louvers | Sq.m | 1 |  |  |  | 0
5.7 | Insulated Plenum boxes 200 x 300 x 650 | Nos | 80 |  |  |  | 0
5.8 | SITC and balancing of grills and deffusers
5.8.1 | 3 slot grills for supply air with hit and miss dampers complete with air patern controller. | RM | 70 |  |  |  | 0
5.8.2 | 3 slot grills for return air without dampers complete with air patern controller. | RM | RO
5.8.3 | Linear Air Grilles with Al. VCD - Linear Fixed Bar Grilles, Horizontal Fixed with removable cores, core styles 1/2/3 way with opposed Blade aluminium Bars, Normal Blade (5 mm nominal thickness) Grille height 16 mm, blade pitch 12.5 mm. 150mm wide linear grilles without dampers | Sq.m | 0 |  |  |  | 0
5.8.4 | Linear Air Grilles without VCD - Linear Fixed Bar Grilles for Return Air 150mm wide linear grilles without dampers | Sq.m | 12 |  |  |  | 0
5.8 | DIFFUSER
a | Supply Air Diffusers with Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction VCD Black Anodized | Nos | RO
b | Return Air Diffusers without Al. VCD - Multicone Ceiling Rectangular Diffusers with removable cores, core styles 1/2/3 way with opposed Blade aluminium extruded construction. | Nos | RO
5.9 | Supply and installation of return air Disc valve (TOILET EXHAUST & FRESH AIR)
| 150dia | Nos | RO
5.10 | Supply Installation testing and comissioning of insulated flexible duct of given sizes. Make Twiga or equal
0
a | Dia 200 | Rmt | 60 |  |  |  | 0
0
5.11 | GI Rings for Flexible Connections
a | 200 Dia | Nos | 160 |  |  |  | 0
b | 300 Dia | Nos | RO
5.12 | Return air Z Piece ( 300 x 300 x 900 ) with Insulation | Nos | RO
6 | INSULATIONS-HVAC
6.1 | Thermal duct insulation :
a | 13mm thick Al.Faced XLPE insulation ('Aerofoam' or approved equivalent) | Sq.m | 350 |  |  |  | 0
6.2 | Duct Accoustic Insulation
a | Acoustic insulation of Ducts - Physically crosslinked Open cell polyolefin foam with factory applied reinforced aluminium foil having density of 25kg/m3 and meeting the Class 0 requirements of Fire safety as per BS 476 Part 6 & 7.The material shall be antifungal in nature and tested to ASTM G21 standard The NRC of 15mm thick material would be 0.4 when tested as per ISO 354 standard. 25mm ( Self Adhesive Only ) Approved Makes - Aerofoam / Thermobreak or equal | Sq.m | 125 |  |  |  | 0
6.3 | Under deck Insulastion
a | Insulation material shall be Closed Cell Elastomeric Armaflex Nitrile Rubber, Density of Material shall be between 45 + 5 kg/m3, Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.035 W/mK at mean temperature of 0C,• The insulation shall have fire performance such that it passes Class 1 as per BS476 Part 7 for surface spread of flame and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire category, Material should be FM (Factory Mutual), USA approved, Moisture Diffusion Resistance Factor ‘µ’ value should be minimum 7000For Concrete Slab: 25 mm thick sheet is used & For Corrugated or metal ceiling: 32 mm thick sheet | Sq.m. | 330 |  |  |  | 0
7 | Scaffolding for Ducting work at Double height area. | Lot | 1 |  |  |  | 0
[5 empty] | Sub Total | 0 | 0
[5 empty] | Total |  | 0
Taxes Extra as applicable