## Electrical_BOQ
ELECTRICAL AND ELV BOQ
SR NO | DESCRIPTION | UNIT | QTY | UNIT RATE | TOTAL AMOUNT
I | MAIN PANEL & SWITCHGEAR ( MAKE DB ELECTRICALS PVT LTD )
1 | Supply, Installation, Testing & Commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process & duly powder coated using Siemens Grey shade no. RAL- 7032. The frame structure & gland Plate(!4g) & doors, partitions shall be with 1.6mm thick CRCA sheet (16g). Base channel of size 75x40x6 mm of ISMC shall be provided. The panel shall be dust & vermin proof with neoprene gasketing. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus-bar shall be of Aluminium (E91) with Epoxy supports & shall be insulated with color coded heat shrink sleeves. The Panel shall be provided with CT's, phase indication lamps, meters, relays & all switchgear, etc as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant.
1.1 | Supply, Installation, Testing & Commissioning of MAIN LT PANEL as per SLD | Nos | 1 |  | 0
1.2 | Supply, Installation, Testing & Commissioning of KITCHEN PANEL as per SLD | Nos | 1 |  | 0
1.3 | Supply, Installation, Testing & Commissioning of APFC PANEL as per SLD | Nos | 1 |  | 0
2 | Supply, Installation, Testing & Commissioning of switchgear with enclosure which shall be dust & vermin proof & with blank plates if required as per the final approval of Consultant.
a | 250 A TPN MCCB Thermal magnetic type (25KA) in MS powdercoated enclosure complete with all mounting accessories like cable end box etc. as per site requirement. | Nos. | 0 |  | 0
b | 100 A TPN MCCB Thermal magnetic type (16KA) in MS powdercoated enclosure complete with all mounting accessories like cable end box etc. as per site requirement. | Nos. | 0 |  | 0
c | 63 A 4P RCCB 300mA type In Enclosure Outdoor Type (IP–65-Model No.601994) for AC Outdoor Unit. | Nos. | 8 |  | 0
d | 40 A 4P RCCB 300mA type In Enclosure Outdoor Type (IP–65-Model No.601994) for AC Outdoor Unit. | Nos. | 0 |  | 0
e | 25 A 4P RCCB 300mA type In Enclosure Outdoor Type (IP–65-Model No.601994) for AC Outdoor Unit. | Nos. | 3 |  | 0
f | SCAME ominia series switched socket outlets with interlock, flush mounting back box, frame complete with gasket. IP 67 Rating 32 A 2 pin & Earth Socket outlet & plug. | Nos. | 12 |  | 0
g | SCAME ominia series switched socket outlets with interlock, flush mounting back box, frame complete with gasket. IP 67 Rating 32 A 3 phase + Neutral & Earth Socket outlet & plug. | Nos. | 12 |  | 0
| TOTAL FOR MAIN PANEL & SWITCHGEAR |  |  | Rs. | 0
II | DISTRIBUTION BOARDS
Supply, Installation, Testing & Commissioning of Distribution boards surface / flush mounted with Double Door containing MCB/ELMCB as incomer and SP MCB as outgoing. All MCB's are of 10KA breaking capacity & ELMCB/RCCB should be of 30mA/100mA sensitivity. The DB shall have appropriate no. of top & bottom knock outs for outgoing circuits & shall be complete with necessary bus-bars, interconnection terminals & earth studs. All terminations in DB shall be complete with ferulling, dressing & all circuits shall be properly labelled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB & MCB shall be 'D' type and other MCBs shall be 'C' category for lighting & raw power use. (LEGRAND MAKE)
1 | Normal Power & Light DB | Nos | 5 |  | 0
6 way TPN DB - Model NO. 507671
Incomer : 1 X 63A 4 POLE MCB
Sub Incomer : 3 X 40A 2P RCCB-100mA
Outgoing : 12 # 10/16/20 A SP MCB 'C' Type
| TOTAL FOR DISTRIBUTION BOARDS |  |  | Rs. | 0
III | CABLES AND ACCESSORIES
Supply and installation of following LT cables rated for 600/1100 volt AC as per IS standard1554 part-I with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20mtr. & then finally with metal identification tags showing the size & the location from/to the specific Panel/DB, at both the ends.
1 | 31/2C x 240 Sq. mm Al. conductor armoured cable | Mtr | 0 |  | 0
2 | 3.5C x 95 Sq. mm Al. conductor armoured cable | Mtr | 0 |  | 0
3 | 4C x 50 Sq. mm Al. conductor armoured cable | Mtr | 0 |  | 0
4 | 4C x 25 sq.mm. Al. conductor armoured cable | Mtr. | 0 |  | 0
5 | 4C x 10 sq.mm. Copper conductor armoured cable - AC Unit, DB etc. | Mtr. | 500 |  | 0 | 50
6 | 4C x 6 sq.mm. Copper conductor armoured cable - AC Unit, DB etc | Mtr. | 220 |  | 0
7 | 3C x 6 sq.mm. Copper conductor armoured cable | Mtr. | 0 |  | 0
7 | 4C x 4 sq.mm. Copper conductor armoured cable. | Mtr. | 140 |  | 0
8 | 3C x 4 sq.mm. Copper conductor armoured cable. (AC, Power socket) | Mtr. | 0 |  | 0
9 | 3C x 2.5 sq.mm. Copper conductor armoured cable (AC, Power socket) | Mtr. | 140 |  | 0
10 | 3C x 1.5 sq.mm. Copper conductor armoured cable (AC, Power socket) | Mtr. | 275 |  | 0
10 | Terminations for following sizes of cables :
Termination of the below sizes of cables with Heavy duty double compression Brass cable glands & Alluminium or copper heavy duty lugs as per requirements. (4c/3.5c/3c)
a | 31/2C x 240 Sq. mm Al. conductor armoured cable | Nos. | 2 |  | 0
b | 3.5C x 95 Sq. mm Al. conductor armoured cable | Nos. | 1 |  | 0
c | 3.5/4C x 50 Sq. mm Al. conductor armoured cable | Nos. | 1 |  | 0
d | 4C x 25/16 sq.mm. Al.conductor armoured cable. | Nos. | 24 |  | 0
e | 3c/4C x 10/16 sq.mm. Copper conductor armoured cable - AC Unit, DB etc. | Nos. | 24 |  | 0
f | 3c/4C x 6/4 sq.mm. Copper conductor armoured cable. | Nos. | 10 |  | 0
g | 4c/3C x 2.5/1.5 sq.mm. Copper conductor armoured cable (AC, Power socket) | Nos. | 20 |  | 0
| TOTAL FOR CABLES AND ACCESSORIES |  |  | Rs. | 0
IV | WIRING & ACCESSORIES –
Supply, installation, testing & commissioning of wiring for light points, power points including Circuit wiring from Distribution Board upto switch board or first light point for circuits controlled directly by MCB and shall be measured on per point basis as primary point in numbers. Similarly Secondary points shall also be measured in nos. and shall include the remaining light points of the circuit. If two switch boards are looped on the same circuit but located at a distance of more than 10 mtrs., then wiring shall be measured as primary points ( 2 nos) NOTE: (Location of Distribution Board and switches are shown on the drawing are indicative and these can get change as per the site conditions. No extra cost shall be paid to the contractor for any such change. All PVC conduit pipes shall be RIGID & MMS type and wires shall be of FRLS or FR type)
1 | PRIMARY POINT WIRING from switch board to first light point in 25 mm dia. PVC conduit using 2 x 1.5 sq. mm PVC insulated copper wires and 1.5 sq. mm green color PVC insulated copper wire for earthing. Conduits to be surface mounted on ceiling, concealed in wall or through partitions of cabins, complete with junction box/pull box. Ceiling - rose or brass light holder and proper clamping as per the final approval of Architect / Consultant (Wires shall be FRLS type)-Average length upto 1st light from switchboard considered upto 10 mtrs). The cost of Modular type switch, plate, box etc. covered elswhere in the offer) | Nos | 55 |  | 0
2 | Providing point wiring for Secondary light points using 2 x 1.0 sq. mm copper conductor PVC insulated wires and 1.0 sq. mm PVC insulated green color copper earth wire for continuous earthing up to fixture in PVC conduits of 20 mm dia, surface mounted on ceiling, concealed in wall and or through partitions with necessary boxes / pull boxes, ceiling rose or light holder and proper clamping complete as per the final approval of Architect / Consultant (Wires shall be FRLS type ). The average lenght from primary point to nearest secondary point considered as 7 mtrs.) | Nos | 350 |  | 0
3 | Providing Automation light points wiring using 2 runs x 2.5 sq. mm copper conductor PVC insulated wires and 1 run of 2.5 sq. mm PVC insulated green colour copper earth wire for continuous earthing upto fixture & switch board in PVC conduits of 20 mm dia, surface mounted on ceiling, concealed in wall and or through partitions with necessary boxes / pull boxes, ceiling - rose or bright light holder and proper clamping complete as per the final approval of Architect / Consultant ( Wires shall be FRLS type ) | Mtr | 2000 |  | 0
6 | Providing Automation Light light points using 2 core x 1 sq. mm copper conductor PVC insulated flexible cable upto fixture from automation DB in PVC conduits of 20 mm dia, surface mounted on ceiling, concealed in wall and or through partitions with necessary boxes / pull boxes etc. complete as per the final approval of Architect / Consultant ( Wires shall be FRLS type ) | Mtr | 500 |  | 0
5 | Providing wiring in existing conduits 3 runs of 2.5 sq.mm. PVC insulated wires FRLS grade for Power socket outlets. | mtr | 1000 |  | 0
6 | Providing wiring in existing conduits 2 runs of 4 sq.mm. & 1 runs of 2.5 sq.mm.PVC insulated wires FRLS grade for Power socket outlets. | mtr | 500 |  | 0
7 | Providing 3 core x 2.5 sq.mm. PVC insulated flexible cables for Power socket outlets through existing conduits/trays/raceways. | mtr | 1500 |  | 0
8 | Providing 3 core x 4 sq.mm. PVC insulated flexible cables for Power socket outlets through existing conduits/trays/raceways. | mtr | 1000 |  | 0
9 | Supply & Installation of Hot dipped Cable Tray complete with necessary fixing arrangements like threaded rod,or angle supports, Anchor Fastner and all other accessories, as per the final approval of the Consultant/Architect.
a | 150 x 50 x1.6 mm Ladder type Cable tray. | Mtr | 20 |  | 0
b | 300 x 50 x1.6 mm Ladder type Cable tray. | Mtr | 100 |  | 0
c | 150 x 50 x1.6 mm Perforated type Cable tray. | Mtr | 30 |  | 0
d | 300 x 50 x1.6 mm Perforated type Cable tray. | Mtr | 50 |  | 0
10 | Supply & installation of AL raceway with 1.6 mm thickness & having fixed with clamps at appropriate intervals & as per the route approved by Architect / Consultant. (Cost of cutting the floor for laying of raceways to be included wherever required) DATA & ELECTRICAL
| a) 1 Runs of underfloor Electrical Al. raceways of size 63x38 mm | Mtr | 100 |  | 0
| b) 1 Runs of underfloor Data Al. raceways of size 100x40 mm | Mtr | 100 |  | 0
11 | Supply & installation of GI junction boxes with 2mm thickness, openable cover on top & having screw-fixed plates on all four sides with knock-out holes for conduits. The plates shall be retained on the sides having no conduit or raceway so as to avoid the entry of any unwanted material. Earth stud to be provided for all Junction boxes for earthing. Junction box to be approved from Architect / Consultant before.
| a) suitable for 550 x 550 x 50 /65 | Nos | 1
| b) suitable for 450 x 450 x 50 /65 | Nos | 1 |  | 0
| c) suitable for 350 x 350 x 50 /65 | Nos | 1 |  | 0
| d) suitable for 300 X 300 x 50 / 65 | Nos | 5 |  | 0
| e) suitable for 150 X 150 x 50 / 65 | Nos | 5 |  | 0
12 | Supply & Installation of 25mm.dia. Medium gauge (MMS) PVC conduit with pull box/ junction box & all accessories for Voice / Data & Power wiring as per the requirement. | Mtr | 500 |  | 0
13 | Supply & Installation of 25mm.dia. PVC flexible conduit pipe | Mtr | 50 |  | 0
14 | Supply, Installation, Testing & Commissioning of flush mounted plate type switch & switch + sockets with hot dipped GI box complete as per the final approval of Architect / Consultant.
a | 6A One way plate type switch - SWITCH Myris NG Black color finish. | Nos | 30 |  | 0
b | 3M Plate for above Switch - Myris NG & Plate Pearl Chapagne or black color finish. | Nos | 10 |  | 0
c | 3M Box for above Switch - Myris NG. | Nos | 10 |  | 0
d | 6A switch controlling 1 no. 3 pin 6A socket outlet complete with Modular plate & metal back box. Myris or equivalent Plate Pearl Chapagne cover plate or black color finish | Nos | 5 |  | 0
e | 2 nos. x 16A switch controlling 2 nos. 6 pin 6/16A socket outlet complete with Modular plate & metal back box. Myris or equivalent Plate Pearl Chapagne or black finish cover plate | Sets | 20 |  | 0
f | 2 nos. 16A switch controlling 2 nos. 6 pin 6/16 A socket outlet complete with Modular plate & metal back box. Myris or equivalent WHITE | Nos | 20 |  | 0
g | 1 x 16A switch controlling 1 no. 6 pin 6/16 A socket outlet complete with Modular plate & metal back box. Myris or equivalent WHITE | Nos | 5 |  | 0
i | 6A switch controlling 1 no. 3 pin 6A socket, 1no. C Power outlet, 1 no. USB outlet,1 no. Blank plate complete with Modular plate & metal back box. Myris NG & Plate Pearl Chapagne or black color finish. | Nos | 5 |  | 0
h | Back box suitable for mounting Network Outlets. | Nos | 5 |  | 0
15 | Arranging temporary Power & Lighting for all agencies to work including suitable protection through MCBs/ELCBs/MCCBs & wiring & cabling. The temporary switch Boards should have minimum 4 Nos of 6A/16A Switch sockets plus two nos of Metal Clad sockets (Single Phase) & one 3 Phase 16A, 5 Pin Metal socket or 16A 3Phase MCB at each location. The Temporary Lighting shall have an average of 150 to 200 Lux at all places maintained. Temporary Power required is approx 20 Kw per floor, which shall be connected to the Tap-off arrangement at each floor. | Lumpsum | 1 |  | 0
| TOTAL FOR WIRING & ACCESSORIES |  |  | Rs. | 0
VI | EARTHING
1 | Supplying and erecting GI strip of 25 x 6 mm used for earthing on wall with necessary MS clamps fixed on wall painted with bituminous paint in an approved manner (Joints are to be Bolted / Welded ) | Mtr. | 100 |  | 0
2 | Supplying and erecting Earth tap off box with Cu strip of 30 x 6 mm of 300mm length in 350X200X85 box with acralic facia used for earthing on wall with necessary clamps fixed on wall painted with bituminous paint in an approved manner (Joints are to be tinned and revetted) | Nos. | 2 |  | 0
3 | Supplying and erecting bare copper conductor of 14 SWG for earthing purpose of DBs & AC machine | Mtr | 300 |  | 0
| TOTAL FOR EARTHING |  |  | Rs. | 0
VIII | LOW VOLTAGE SYSTEM
1 | ADDRESSABLE FIRE ALARM SYSTEM( RAVEL MAKE - UL APPROVED)
a | 2 Loop Addressable Fire Alarm Panel: Intelligent Fire Alarm Control Panel - Addressable Devices, Bell Circuit, Integrated PSU with Battery Charger & Batteries, (Certificated by LPCB or UL) | Nos. | 1 |  | 0
b | Addressable Manual Call Point Semi FlushMounting Re-settable, Supplied with Special Reset Tool | Nos. | 3 |  | 0
c | Addressable Combined Sounder and Strobe, Loop Powered and 24VDC. | Nos. | 3 |  | 0
d | Addressable Smoke Detector Intelligent Optical Detector, Above False/Below Ceiling | Nos. | 70 |  | 0
e | Addressable hEAT Detector, Above False/Below Ceiling | Nos. | 5 |  | 0
f | Response Indicator for AFC Detectors | Nos. | 20 |  | 0
g | AUTO DIALLYING System | Nos. | 0 |  | 0
h | Short Circuit Isolator Module | Nos. | 3 |  | 0
i | Addressable Relay Module. | Nos. | 3 |  | 0
j | MS Junction Box with GI Glands for AFC & True Ceiling Detectors & Modules | Nos. | 40 |  | 0
k | Supply, installation of 2C x 1.0 sq. mm FRLS armoured cable RED in color for Fire Alarm Works System. The cost is inclusive of termination as per standard practice or as advised by Consultant. MAKE -CENTURY CABLE | Mtr | 1050 |  | 0
| SUB TOTAL FOR FIRE ALARM SYSTEM |  |  | Rs. | 0
2 | CCTV SYSTEM cabling
1 | SITC of CAT 6 - 4 Pair UTP Cable (1 Box = 305 Mtrs ) ( Make : COMMSCOPE ), including termination, connection, testing etc | Mtr | 610 |  | 0
2 | Co-ordination charges for CCTV equipments. | LS | 1 |  | 0
| SUB TOTAL FOR CCTV EQUIPMENTS |  |  | Rs. | 0
3 | DJ CONSOLE & PROJECTOR/TV CABLING:
1 | Removing & relaying speaker/MIC cables as directed by Architect/Consultants.(Labour charges only) | Mtr | 100 |  | 0
2 | Removing & relaying HDMI cables as directed by Architect/Consultants.(Labour charges only) | Mtr | 100 |  | 0
3 | Removing & relaying Power cables as directed by Architect/Consultants.(Labour charges only) | Mtr | 100 |  | 0
| TOTAL FOR PA SYSTEM |  |  | Rs. | 0
4 | TELEPHONE SYSTEM – MAIN WIRING
1 | Supply & Installation of 25mm.dia. Medium gauge (MMS) PVC conduit with pull box/ junction box & all accessories for Voice / Data & Power wiring as per the requirement. | Mtr | 500 |  | 0
2 | 25 dia flexible conduit | Mtr. | 75 |  | 0
3 | Supply, installation of CAT 6 - 4 Pair UTP Cable ( 1 Box = 305 Mtrs ) ( Make : COMMSCOPE ) | Mtr. | 305 |  | 0
4 | Testing of all Terminations using Fluke Cable Analyser. The cost quoted is including Information outlet. | Nos | 8 |  | 0
5 | Supply & Installation of Dual I/O Face Plate ( Make : COMMSCOPE ) | Nos | 8 |  | 0
6 | Supply & Installation of CAT 6 I/O ( Make : COMMSCOPE ) | Nos | 8 |  | 0
7 | Telephone patch cord | Nos. | 8 |  | 0
| TOTAL FOR TELEPHONE DISTRIBUTION |  |  | Rs. | 0
5 | DATA (NETWORK SYSTEM)
1 | Supply, installation of CAT 6 - 4 Pair UTP Cable ( 1 Box = 305 Mtrs ) ( Make : COMMSCOPE ) | Mtr. | 610 |  | 0
2 | Testing of all Terminations using Fluke Cable Analyser. The cost quoted is including Information outlet. | Nos | 8 |  | 0
3 | Supply & Installation of Dual I/O Face Plate ( Make : COMMSCOPE ) | Nos | 8 |  | 0
4 | Supply & Installation of CAT 6 I/O ( Make : COMMSCOPE ) | Nos | 8 |  | 0
5 | Supply, Installation, testing & commissioning of 48 port patch panel ( Make : COMMSCOPE ) | Nos. | 0 |  | 0
6 | Supply, installation of 1 Mtr UTP Patch Cord CAT 6 ( Make : COMMSCOPE ) | Nos | 8 |  | 0
7 | Supply, installation of 2 Mtr UTP Patch Cord CAT 6 ( Make : COMMSCOPE ) | Nos | 8 |  | 0
8 | Supply, installation of 5 Mtr UTP Patch Cord CAT 6 ( Make : COMMSCOPE ) | Nos | 0 |  | 0
9 | PVC Horizontal Cable Manager | Nos | 0 |  | 0
10 | Jack panel 24 Port (Voice & Data) | Nos | 1 |  | 0
11 | Supply, Installation of 6 core multimode armoured OFC cable on existing cable tray (Make : COMMSCOPE) | Mtr. | 0 |  | 0
12 | OFC : Termination of Fiber Cores using Fusion Splicing Method | Nos. | 0 |  | 0
13 | OFC : Testing of Fiber Cores After Termination | Nos. | 0 |  | 0
14 | Documentation: Includes Updation of Drawing Specifying Data, Voice Points on Floor Plan, Soft Copy & Hard Copy of all Test Reports Certification: 20 year performance guarantee Certificate by Schneider ensuring installation is done as per TIA/EIA or ISO/IEC standards & will support the application(s) which the system was designed to support. | LS | 1 |  | 0
15 | HEAT MAP ANALYSIS TEST FOR WIFI NETWORK : Test to plan and create Wi-Fi networks according to client performance and capacity requirements and simulating real-life application usage such as VoIP, HD video streaming and web browsing. | LS | 1 |  | 0
| TOTAL FOR NETWORKING: |  |  | Rs. | 0
V | LIGHTING FIXTURES: Labour charges towards Installation Only |  |  |  |  | provisional
a | Linear profile light for ceiling Cove light | mtr. | 165 |  | 0
b | Flexible profile light for Cove light for wall paneling/skirting etc. | mtr. | 100 |  | 0
c | Wall mounted light/Ceiling mounted decorative indoor lights. | Nos. | 20 |  | 0
d | Decorative table lamps | Nos. | 10 |  | 0
e | Spot light upto 24 Watts | Nos. | 66 |  | 0
e | Spot light upto 12/15 Watts | Nos. | 100 |  | 0
f | Decorative outdoor 3 watt uplighter | Nos. | 200 |  | 0
g | 6w grazer spot light | Nos. | 20 |  | 0
h | Submersible light for waterbody | Nos. | 15 |  | 0
i | Occupancy sensor for Washroom | Nos. | 4 |  | 0
j | LIGHTING AUTOMATION PROVISIONAL BUDGET. | LS
| TOTAL FOR LIGHTING FIXTURES |  |  | Rs. | 0 | 0