## VENT
PROJECT : LOUNGE , TRIVANDRUM AIRPORT
SUMMARY TO SCHEDULE OF PRICES - VENTILATION WORKS R1
Amount(Rs.)
Part A | Hi Side Works |  |  |  | 0
Part B | Low Side Works |  |  |  | 0
| Grand Total |  |  |  | 0
PROJECT : LOUNGE , TRIVANDRUM AIRPORT
SCHEDULE OF PRICES - VENTILATION WORKS R1
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part A | Hi Side Works
1 | Kitchen Scrubber (Dry Type)-With Fan Section
1.1 | Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)
The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12.5 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
Power Consumption : Not more than 50W per cell.
Capacities : 3000 CFM
1.2 | DIDW Blower
DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications & Drawings
1.3 | Casing
Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42Kg/Cum with 0.6 mm pre-plasticized /pre-coated Galvanised steel sheet outside & 0.6 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately housed both Electrostatic Modules and Fan with Drive.
1.4 | Accessories
The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt & pulleys, vibration isolators, internal frame works ,canvas connection, Inlet/Outlet flange connection etc
Note: The Dry Scrubber shall be a single unit with 1x3000 CFM Dry Scrubber and DIDW Blower
| 5100 CMH (3000 CFM) DIDW Blower Capacity at 80 MM ESP 2.25 KW (3 Phase) motor | Nos | 1 |  | 0
2 | AHU Fan Section
2.1 | Supply, Installation, Testing and Commissioning of Double Skin Type AHU Fan section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside with 25mm injected PUF insulation of 38KG/m3 , G.I. blower section, VFD Operated Plug Fans with motors , base , drive arrangement ,Filter, motor drive suitable for Outdoor Application complete as per specifications and drawings .
2.1.1 | 2500 CFM (with Backward Curve Type DIDW Blowers 1.5 KW Motor ; ESP 30 mm of wg | Nos | 1 |  | 0
3 | Inline Fans (Cabinet Type with acoustic enclosure)
3.1 | 200 CFM at 15 MM ESP | Nos. | 1 |  | 0
| Sub-Total Part-'A' Rs. |  |  |  | 0
Part B | Low Side Works
2 | DUCTING
2.1 | G.I. Sheet Metal Ducting - Factory Fabricated
Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
i. | 0.50 MM (26 Gauge) | Sqm. | 40 |  | 0
ii. | 0.63 MM (24 Gauge) | Sqm. | 50 |  | 0
iii. | 0.80 MM (22 Gauge) | Sqm. | 10 |  | 0
iv. | 1.00 MM (20 Gauge) | Sqm. | R.O.
v. | 1.25 MM (18 Gauge) | Sqm. | RO
2.2 | G.I. Sheet Metal Ducting - Site Fabricated
Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
i. | 0.63 MM (24 Gauge) | Sqm. | 10 |  | 0
ii. | 0.80 MM (22 Gauge) | Sqm. | 5 |  | 0
iii. | 1.00 MM (20 Gauge) | Sqm. | RO
iv. | 1.25 MM (18 Gauge) | Sqm. | RO
3 | INSULATION
3.1 | Nitrile Rubber Insulation- Class 'O'
Supplying and fixing of closed cell elastomeric insulation of density 55 kg/cu.m.and K valueof not less than 0.037W/mk at 20 deg C as per specifications and drawings (For indoor applications) with factory Laminated 7 mill woven glass cloth
i. | 19 mm thick (Fresh Air Ducts) | Sqm. | 25 |  | 0
ii. | 25 mm thick (Exhaust Air ducts) | Sqm. | 55 |  | 0
3.2 | Acoustic Lining
Supplying and Application of Acoustic lining within the Supply Air duct with 15 mm thick class 'O' open cell nitrile Rubber of density 140-160 kg./Cubm. as per spefications.
i. | 15 MM Thick | Sqm | RO
4 | DUCT ACCESSORIES
i. | Supply, Installation, Testing and Commissioning of GI multiblade volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 1 |  | 0
ii. | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Supply / Exhaust Air Grills with damper as per specifications | Sq.m | 0.6 |  | 0
iii. | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Supply Air Diffuser with damper as per specifications | Sq.m | RO
iv. | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Return Air Diffuser without damper as per specifications | Sq.m | RO
v. | Supply, Installation, Testing and Commissioning of Exhaust Air Opening damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications | Sqm | 1 |  | 0
vi. | Supply, Installation, Testing and Commissioning of multiblade Al volume control Collar / Grille damper complete with suitable links, lever and quadrants for manual control of airflow and with suitable links , lever and quadrants for manual control of airflow and neoprene rubber gaskets, nuts, bolts, screws, flanges etc., as per specifications. | Sqm. | RO
vii. | Supply, Installation, Testing and Commissioning & fixing of powder coated extruded Aluminium Continuous Grille as per specifications
a.) | Continuos Grille 100MM Wide | RM | RO
b.) | Continuos Grille 200MM Wide | RM | RO
5 | Canvas
i. | Supply & Installation of double skin fire retardant canvas connection for AHU Fan Section , Exhaust Units , Ductable Units etc. | Sqm. | 6 |  | 0
6 | Louvers
i. | Providing and fixing of powder coated extruded aluminium exhaust air louvers/ fresh air louvers with bird screen and mounting arrangement as per specification and drawings. Free Area shall be more than 60% of gross area.
a.) | Fresh Air / Exhaust Air Louvers with Bird Screen Mesh | Sqm. | R.O.
| Sub-Total Part-'B' Rs. |  |  |  | 0

## SUMMARY
PROJECT : LOUNGE , TRIVANDRUM AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS R1
Amount(Rs.)
Part A | VENTILATION WORKS | 0
| Grand Total | 0