## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
B | AC PIPING
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make: Astral, Supreme or equivalent with airport approval).
B.1.1 | 25 mm Ø | Mtr | 20
B.1.1 | 32 mm Ø | Mtr | 25
HVAC WATER PIPING
B.2 | Supply, installation and testing of MS class (C) Pre-Insulated Chilled Water Pipe with Poly urethane foam (PUF) insulation of minimum 36 kg/cu.m density and AL jacket or cladding with all necessary fittings, connections, flanges and all necessary pipe supports, clamps as applicable and as per site conditions. (Make: Jindal (Hissar), Tata Steel, SAIL or equivalent with airport approval).
B.2. | 40 mm Ø (Insulation thickness - 32 mm) | Mtr | 36
B.2.2 | 32 mm Ø (Insulation thickness - 32 mm) | Mtr | 26
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.1.1 | 22 Gauge - (0.85 mm Thick) - Supply Air Duct | Sq.Mtr | 40
C.1.2 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 23
C.1.3 | 22 Gauge - (0.85 mm Thick) - Make-Up Air Duct | Sq.Mtr | 40
C.1.4 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.Mtr | 40
C.1.5 | 22 Gauge - (0.85 mm Thick) - Return Air Duct | Sq.Mtr | 20
C.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 60
ROUND DUCTS
C.3 | Supply, installation, and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) factory fabricated Spiral Round Ducts with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
C.3.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 22
FLEXIBLE DUCTS
C.4 | Supply, installation, and testing of aluminium-polyester casig Round Flexible Duct reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard insulation thickness of 25 mm and with all necessary connections, fixing and support arrangements of approved make.
C.4.1 | 300 mm Ø | Mtr | 28
C.5 | Supply, installation, and testing of Flexible Duct Connectors to isolate vibrations and noises caused by air handling units , fans or any other equipments connected to the duct with air tight fittings with all necessary accessories.
C.5.1 | For AHU | Nos | 3
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
D.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.1.1 | 19 mm thicknesses - (SAD) - External Duct Insulation | Sq.Mtr | 60
D.1.2 | 19 mm thicknesses - (MUAD) - External Duct Insulation | Sq.Mtr | 75
D.13 | 19 mm thicknesses - (RAD) - External Duct Insulation | Sq.Mtr | 20
D.2 | Supply, installation & testing of Thermal Insulation of ducting using Aluminium foil faced resin bonded fibre Glass wool of density not less than 48 kg/m3. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.2.1 | 80 mm thicknesses - (KED) - External Duct Insulation | Sq.Mtr | 50
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
D.3 | Supply, installation & testing of Acoustic Insulation of ducts using opencell processed elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.045 W/(m-K) at 0° C and Fire performance according to building regulations - Class 1 as per BS 476, with very good sound absorption, damping and barrier properties. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.3.1 | 15 mm thicknesses - (SAD) - Internal Duct Lining | Sq.Mtr | 18
E | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Opposed Blade Damper / Collar Damper with Nylon gears and lever on face side for smooth operation. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
E.1.1 | Size - 500 x 500 mm | Nos | 7
E.1.2 | Size - 500 x 250 mm | Nos | 1
E.1.3 | Size - 300 x 250 mm | Nos | 10
E.1.4 | Size - 300 x 200 mm | Nos | 1
E.1.5 | Size - 250 x 250 mm | Nos | 9
E.1.6 | Size - 250 x 200 mm | Nos | 1
F | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
F.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Square Grille with fixed Aerofoil Blades, with 30° deflection - 1 Way with rigid frame of 16mm flange as standard. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.1.1 | Neck Size - 500 x 500 mm | Nos | 7
F.1.2 | Neck Size - 200 x 200 mm | Nos | 1
F.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Rectangular Grille with fixed Aerofoil Blades, with 30° deflection - 1 Way with rigid frame of 16mm flange as standard. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 900 x 400 mm | Nos | 2
F.2.2 | Neck Size - 800 x 400 mm | Nos | 1
CEILING DIFFUSERS
F.2 | Supply, installation, tetsing and commissioning of Aluminium Round Diffuser with circular cones for throw in circular patern and inbuild butter fly damper, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 350 mm Ø | Nos | 21
G | TESTING & COMMISIONING
G.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1