## High side HVAC BOQ
NAME OF PROJECT: Land side Central Kitchen at Hyderabad
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE |  | AMOUNT
|  |  |  | Supply | Installation | Supply | Installation
1 | KITCHEN EXHAUST AIR SCRUBBER
Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications.
Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type SS Filters with aluminium mesh filters, Tungsten wire type type ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area, collection area should not be less than 6.0 sqmt, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state and entier unit should be CE Certified. all units shall have shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety. The units should be BMS compatible for Feedback information on Run,Wash and Fault,dry contact point. The system should allow connection to a fan section to achieve velocity between 2.5 - 3.8 m/s across the air cleaner and should units should meet MERV 15 requirements even at velocity of 3.81 m/s (750 FPM)
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
ESP Power Consumption : Not more than 50W per cell.
Air Moving Capacities are as follows:
| 10800 CFM | No. | 1
GRAND TOTAL

## Low side HVAC BOQ
NAME OF PROJECT: Land side Central Kitchen at Hyderabad
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 18 G sheet | sq.m | 100
| 20G sheet | sq.m | 10
| 22G sheet | sq.m | 10
| 24G sheet | sq.m | 90
| 26G sheet | sq.m | 5
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 18 G sheet | sq.m | 10
| 20G sheet | sq.m | 5
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 10
3 | THERMAL INSULATION FOR KITCHEN DUCTS
SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade.
| 80 mm Thick | sq.m | 130
4 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 5
5 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 0.5
GRAND TOTAL

## MAKE LIST
NAME OF PROJECT: Land side Central Kitchen at Hyderabad
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Thermal Insulation on Kitchen Duct | UP Twiga, Owens Corning, Supreme
9 | Dry Scrubber | Rydaire / Trion / Halton
10 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
11 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
12 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
13 | Cables | Polycab / Finolex / Hawells
14 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
15 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech