## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
1 | KITCHEN EXHAUST AIR SCRUBBER
Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type SS Filters with aluminium mesh filters, Tungsten wire type type ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area, collection area should not be less than 6.0 sqmt, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state and entier unit should be CE Certified. all units shall have shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety. The units should be BMS compatible for Feedback information on Run,Wash and Fault,dry contact point. The system should allow connection to a fan section to achieve velocity between 2.5 - 3.8 m/s across the air cleaner and should units should meet MERV 15 requirements even at velocity of 3.81 m/s (750 FPM) Operating Voltage : 220V, 50 Hz Ionizing Voltage : 12 to 13 KVDC Collector Cell Voltage : 6 to 6.5 KVDC ESP Power Consumption : Not more than 50W per cell. Air Moving Capacities are as follows:
| 10800 CFM | No. | 1