## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
B | HVAC EQUIPMENTS AC EQUIPMENT (CHILLED WATER - TYPE)
B.1 | Supply, installation, testing and commissioning of Chilled water type Double Skinned, Thermal break , Eurovent certified ceiling suspended Air Handling Units approved make with minimum 40 mm thick panels of 40-42 Kg density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, filter section with EU4 Pre Filter, coil section with 4 RD chilled water cooling coil with aluminum fins, and fan section with direct driven backward curved Plenum plug fan with aerofoil design blades with VFD, insulated SS304 18 gauge auxiliary drain pan, including control panel. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply with all necessary mounting and fixing arrangements for the equipment including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS), Fan outlet velocity shall not exceed 2000 FPM (10 MPS). Quote shall be inclusive of wired remote controller with LCD/LED digital display. Note : External Static Pressure (ESP) is calculated based on design drawing however contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.1.1 | 10.0 TR - (3000 CFM @ 120-150 PASCAL -ESP) | Nos | 1