## ELEC & ELV
BILL OF QUANTITIES
PROJECT: | IN-DXN-SEATING AREA (FOOD MAHAL) | [5 empty] | DATE: | 10.12.2024
[7 empty] | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire, and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING/ INTEGRATING UNIT M&E SERVICES TO AIRPORT M&E SERVICES/ BUILDING
A.1 | If any termination /connection of the unit services are required outside the site location (i.e. connection of the unit M&E to the airport M&E or service termination to the airport external façade/ roof etc.); then the contractor has to work in consultation with the airport to plan, design & detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. |  |  | Provisional Sum
B | METER / METER PANEL
B.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type and compatible with Airport BMS for realtime monitoring, of approved make or any other make with kVAH option with Approval from TS Department.
B.1.1 | 63/5A Energy Meter(Direct)-3 Phase | Nos | 1 |  | 0 |  | 0 | 0
C | LV CABLING
C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed,AL/ Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & earthing). The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench using necessary supporting / clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing.
C.1.1 | 3.5C x 50 Sq. mm XLPE AL Armoured Cable + 2 x 8 SWG CU. | Mtr | 10 |  | 0 |  | 0 | 0
C.1.2 | 4C x 4 Sq. mm XLPE CU. Armoured Cable + 2x10 SWG CU. | Mtr | 160 |  | 0 |  | 0 | 0
D | CABLE END TERMINATIONS
D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete.
D.1.1 | 3.5C x 50 Sq. mm XLP Al. Armoured Cable | Nos | 4 |  | 0 |  | 0 | 0
D.1.2 | 4C x 4 Sq. mm XLPE CU Armoured Cable | Mtr | 14 |  | 0 |  | 0 | 0
E | DISTRIBUTION BOARDS
E.1 | Supply, Installation, Testing & Commissioning of approved make Surface / Flush / Floor mounting 10kA / 25kA Distribution Boards, Devices, Relays and all accessories. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring & earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.), Indicative Devices (Phase Indicative Lamps, kWH Meter, MFM, Voltmeter, Ammeter, Switches, etc.), Control Devices (Bus Coupling Contactors, Earth Leakage, Control, Over Load Relays, Shunt trip coil for BMS, CT, PT, Low Voltage Power Supply Transformers & Protective relays, etc.), Starter Panels (DOL Starters, Star/Delta Starters, Soft Starters, VFD's, etc), Fire Alarm Interfacing circuit devices & relays as per Electrical SLD & Load Calculation Sheet. The DBs shall also be fully compatible with the Building Management System (BMS) for integration into the centralized control system, enabling remote monitoring, status indication, fault detections through communication protocols such as Modbus, BACnet, or other airport-specified protocols. This includes provisions for BMS-compatible meters, relays, and communication interfaces as per BMS design.The DB shall include provisions for future BMS upgrades or modifications as per airport operational changes All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall be Hpi / Si series & MCB's shall be 'B" / 'C' Curve (As per Airport requirement).
E.1.1 | SMDB-COM | Each | 1 |  | 0 |  | 0 | 0
16 Way Three phase Panel board
Incomer
100A FP MCCB - 1 No.
32A 30 mA FP RCBO - 1 No.(Sub Incomer)
Outgoings
10/16/20/25A SP MCB- 18 Nos
16A 30mA 2P RCBO - 6 Nos.
25A 30mA 4P RCBO - 8 Nos.
E.1.2 | UPS DB-01 | Each | 1 |  | 0 |  | 0 | 0
16 Way SPN DB
Incomer
25A 30mA 2P RCBO - 1 No.
Outgoings
10/16/20/25A SP MCB- 12 Nos
F | LIGHT POINT WIRING
F.1 | Supply, Installation, Testing & Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with approved makes Switches / Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660/1100V grade using 2 X 1.5 Sq mm PVC insulated fine stranded single core FRLSH copper conductor wires phase and neutral and with 1.5 Sq mm PVC insulated, green coloured, fine stranded single core copper cable as earth continuity, earth wire crimped to copper socket, fastened using brass bolt and nut etc through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
F.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. | Nos | 8 |  | 0 |  | 0 | 0
F.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) | Nos | 135 |  | 0 |  | 0 | 0
G | CIRCUIT WIRING
G.1 | Supply, Installation, Testing & Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit/ GI Trunking (Containment size & Type selection as per site requirement) for the following types of wires.
G.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit / GI Trunking from DB to Light control switch box/Normal Sockets. | Mtr | 390 |  | 0 |  | 0 | 0
G.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit / GI Trunking from DB to Power points. | Mtr | 100 |  | 0 |  | 0 | 0
H | POWER POINTS (SWITCHES & SOCKETS)
H.1 | Supply, Installation, Testing & Commissioning of approved makes Devices (Switches & Sockets - Face Plate Finish as approved by Architect / Matching to Architecture/interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface / Concealed as per site condition & maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50/60 Hz, AC supply as per Airport / Country power supply.
H.1.1 | 13A Single Switched Socket Outlet | Nos | 0 |  | 0 |  | 0 | 0
H.1.2 | 13A Dual Switched Socket Outlet | Nos | 3 |  | 0 |  | 0 | 0
H.1.3 | 16A Single Switched Socket Outlet | Nos | 2 |  | 0 |  | 0 | 0
H.1.4 | 20A Isolator with suitable metal enclosure | Nos. | 1 |  | 0 |  | 0 | 0
H.1.5 | One Gang Blank Plate | Nos | 1 |  | 0 |  | 0 | 0
J | LIGHTING FIXTURES
J.1 | Supply, Installation, testing and commissioning of approved makes Light fixtures complete with accessories. Rate shall include necessary mounting bracket, suspension chains etc.
J.1.1 | Exit Light (Wall / Ceiling Mounted) | Nos | 3 |  | 0 |  | 0 | 0
K | CONTAINMENT
K.1 | Supply & Installation of approved makes medium duty Hot dip perforated GI Cable Tray, through Wall / Ceiling as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc.
K.1.1 | 300 x 50 mm Cable Tray | Mtr. | 8 |  | 0 |  | 0 | 0
K.1.2 | 150 x 50 mm Cable Tray | Mtr. | 6 |  | 0 |  | 0 | 0
K.1.3 | 100 x 50 mm Cable Tray | Mtr. | 45 |  | 0 |  | 0 | 0
L | UPS SYSTEM
L.1 | Supply, Installation, Testing & Commissioning of approved makes UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) & standard accessories / equipments required for complete functioning of the system, earthing, support system (if required), etc. The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required.
L.1.1 | 5 KVA Single phase UPS with 30 Minute Back-up | Nos. | 1 |  | 0 |  | 0 | 0
M | CCTV SYSTEM
M.1 | Supply, Installation, Testing & Commissioning of approved makes CCTV System with suitable / required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console NVR/DVR with Power Box , Suitable POE with Port switch & Surveillance hard disk,etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
M.1.1 | CCTV ceiling Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. | Nos | 11 |  | 0 |  | 0 | 0
M.1.2 | CCTV wall Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. | Nos | 1 |  | 0 |  | 0 | 0
M.1.3 | Suitable size IDF RACK with Necessary Patch Panel & Network switch as required. | Nos | 1 |  | 0 |  | 0 | 0
M.1.4 | 16-Channel NVR | Nos | 1 |  | 0 |  | 0 | 0
M.1.5 | SITC of CAT6 cable on surface /concealed/ wall, including suitable conduits, fittings, accessories, etc. | Mtr. | 160 |  | 0 |  | 0 | 0
N | DATA NETWORK SYSTEM
N.1 | Supply, Installation, Testing & Commissioning of approved makes Data & Telephone Network System with required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF/SERVER Rack using patch cordes, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
N.1.1 | Single Data outlet (RJ45) Jack | Nos | 0 |  | 0 |  | 0 | 0
N.1.2 | Dual Data outlet (RJ45) Jack | Nos | 3 |  | 0 |  | 0 | 0
N.1.3 | SITC of CAT6 cable on surface /concealed/ wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | Mtr. | 190 |  | 0 |  | 0 | 0
O | PA SYSTEM
O.1 | Supply, Installation, Testing & Commissioning of approved makes PA System with required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
O.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories | Nos | 4 |  | 0 |  | 0 | 0
O.1.2 | Volume Controller | Nos | 1 |  | 0 |  | 0 | 0
O.1.3 | PA Controller with Amplifier | Nos | 1 |  | 0 |  | 0 | 0
O.1.4 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | Mtr. | 40 |  | 0 |  | 0 | 0
P | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
P.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements.
P.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
Q | MISCELLANEOUS
Q.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
Q.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Unit | 1 |  | 0 |  | 0 | 0
Q.1.2 | Provide and Fixing Shock Treatment Chart | Unit | 1 |  | 0 |  | 0 | 0
Q.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side | Unit | 1 |  | 0 |  | 0 | 0
R | SHOP DRAWINGS & APPROVALS
R.1 | Preparation and submission of a detailed shop drawing for the electrical system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, plumbing, and fire services, along with updating SLD, load calculation sheets, and power layouts as per approved, selected, or supplied equipment power and phase requirements, this also needs to be coordinated with latest architectural, structural and interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
S | ANY ADDITIONAL ITEMS
S.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
S.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit |  |  | 0 |  | 0 | 0
S.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit |  |  | 0 |  | 0 | 0
S.1.3 | Item 2 - (Contractor to describe only if there are any) | Unit |  |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.