## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
B | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
B.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc.
B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 26
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
B.2 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc.
B.2.1 | 65 mm Dia | Nos | 1
FIRE SPRINKLER PIPING
B.3 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns)
B.3.1 | 25 mm Dia | Mtr | 35
B.3.2 | 32 mm Dia | Mtr | 18
B.3.3 | 40 mm Dia | Mtr | 10
B.3.4 | 50 mm Dia | Mtr | 5
B.3.5 | 65 mm Dia | Mtr | 8
B.4 | Supply & Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1" (25mm) BSPT/ NPT connection),Outlet Reducer (1/2" (15mm) BSPT / NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc.
B.4.1 | Assembly Length of (1500 mm) | Nos | 26