## Sheet1
A. CIVIL & INTERIOR BOQ-Ahemedabad Airport |  |  |  |  | Area | 600
Task No. |  | Sub Task No. | Name of Item | Description of Item | Unit | Quantity | Rate | Amount | Remark
H |  |  |  | HVAC LOW SIDE
| H.1.0 |  |  | DUCTING : ( MAKE: ZECO/TATA/JINDAL/SAIL/ROLASTAR/NUTECH)
|  |  | a | Supply, Installation, Testing and Commissioning of factory made lock-forming quality flat oval spiral ducting of approved makes complying with IS: 277 and having 120 GSM coating classification with elbows, turning vanes, volume control dampers, G.I. supports, hangers, etc. required accessories . The price shall include the cost of threaded rod supports/Gripples for open ceiling area etc. The item also include providing & applying two coat of approved make anti corrosive paint over a coat of primer as per manufacturers/architect's recommendations.
|  |  | b | Supply, Installation, Testing and Commissioning of Site Fabricated rectangular GI ducting of approved makes complying with IS: 277 and having 120 GSM coating classification. The price shall include the cost of necessary accessories & supports (like flanges, neoprene gaskets, wire ropes, corner saddles, guide vanes, vibration isolators, fire retardant canvas connection in all fan outlet connections, joints, sealing around the duct at wall crossings, labeling, (M.S supports / M.S Frame For Duct travelling Vertical up to Terrace, necessary flange type opening at specific interval for duct cleaning etc. for kitchen exhaust duct )as per specifications. The price shall include the cost of threaded rod support. The item also include providing & applying two coat of approved make anti corrosive paint over a coat of primer as per manufacturers/architect's recommendations,also with cheisling and scaffolding if required.
|  |  | b.1 | 22 gauge galvanized sheet - For Exhaust & fresh Air Duct | Sq.mtr | 15 |  | 0
|  |  | b.2 | 24 gauge galvanized sheet - For Exhaust & fresh Air Duct | Sq.mtr | 30 |  | 0
|  |  | b.3 | SITC of Canvas cloth at fan mouth for Exhaust & Fresh air unit as per detail specification | Nos | 2 |  | 0
| H.2.0 |  |  | THERMAL INSULATION
|  | a |  | Supply & Installation of closed cell structure Elastomeric foam based on synthetic nitrile rubber. The insulation material shall have fire performance of Class O acc. to building regulations. Fire propagation shall be tested acc. to BS476 Part 6:1989. It shall be FM approved & UL94 tested.
|  | a.3 |  | 09 mm thick for External Insulation of Exhaust duct | Sq.mtr | 10 |  | 0
| H.3.0 |  |  | AIR DISTRIBUTION SYSTEM (MAKE: CARRIYAIR, AIRMASTER,COSMOS, RAVISTAR )
|  | b |  | VCD :- Supply, installation, testing and commissioning of 150mm wide GSS Volume Control Dampers with 18G GI casing & 20G GI Blade, complete with chrome plated Spindle lubricating bush and quadrent to suit Manual operation. | Sqft | 3 |  | 0
| H.4.0 |  |  | Exhaust Fan for Toilet supply
|  | a.1 |  | Supplying and erecting fresh air cum Exhaust fan of light duty 250 V A.C. 50 cycles 300mm/400mm. 1400 RPM rust proof body & blades, wiremesh, duly erected in an approved manner.(Havells/Usha/Crompton or Orient.) | Each | 1 |  | 0
|  | a.2 |  | Heavy Duty 450 mm Dia Exhaust Fan (Make Cromptoon & Equivalent) | Each | 1 |  | 0
| H.5.0 |  |  | Additional HVAC Items
|  | a |  | INSULATED DRAIN PIPING
SITC of PVC drain piping with 9mm thick tubular insulation complete with PVC, fitting, accessories etc.
|  | a.1 |  | 25mm dia | Rmt. | 20 |  | 0
|  | a.2 |  | 32mm dia | Rmt. | 10 |  | 0
|  | c |  | Chilled water piping MS `C' class with 25mm thick Nitrile Rubbe insulation. |  |  |  | 0
|  | c.2 |  | 40 mm dia. | Rmt | 5 |  | 0
|  | c.3 |  | 32 mm dia. | Rmt | 5 |  | 0
|  | c.4 |  | 25 mm dia. | Rmt | 40 |  | 0
|  | d |  | Balancing valve with insulation |  |  |  | 0
|  | e |  | Butterfly Valve (with insulation). |  |  |  | 0
|  | e.1 |  | 40 mm dia | Nos. | 4 |  | 0
|  | f |  | Y-strainer with insulation. |  |  |  | 0
|  | g |  | Power / Control Cabling (Max. 5 Rmt.) between Units and 3-way valve. | Sets | 5 |  | 0
|  | g.1 |  | (Any extra length shall be payable @Rs. 300/- per Rmt.) |  |  |  | 0
|  | j |  | STARTER PANEL FOR EXHAUST AIR & FRESH AIR FAN
|  | j.1 |  | Supply, Fabrication, Installation, Testing & Commissioning of HVAC sarter panel for kitchen exhaust fans (As given above) with IP-55 Enclosure comprising of main incoming feeder, 1 nos. of DOL 3-phase starter for exhaust fans, 1 nos. of DOL 3- phase starter for fresh air fans, ON/OFF/Trip indicators, Start/Stop/ Push Buttons, Auto/Manual switch, Voltmeters , NO-NC contacts for integrating of fresh air fan with exhaust air fans, minimum 2 potential free contacts etc. Installation with necessary accessories and required wiring with termination, glanding, lugs comprising etc. | Nos. | 2 |  | 0
I |  |  |  | Miscellaneous work
| I.1.0 |  |  | Extra Frequent Item
|  | f |  | Supply, installation, testing & commissioning of sensor with 180 deg coverage & 1 mtr range used for air curtain complete with all required accessories. Make: Any make readily available with min warranty of 1 year. | Nos | 4 |  | 0
|  | h |  | Providing and fixing water level sensor fully automatic with high and low indicator with alarm (Make : microtail ,OS or equivalent ) | Nos | 2 |  | 0
| I.2.0 |  |  | Fitting / Fixing of following item with necessary arrangement as directed
|  | b |  | Safe/Furniture /Staff locker/IT Rack | Each | 2 |  | 0
|  | c |  | Money box fixing | Each | 1 |  | 0
|  | e |  | Suspension & hanging of Exhaust hood from ceiling | Each | 1 |  | 0
|  | g |  | Pesto flash | Each | 3 |  | 0
|  | h |  | Computer rack | Each | 3 |  | 0
|  | i |  | Strip curtain for oven hood | Job | 1 |  | 0
|  | j |  | Strip curtain for cold room | Job | 1 |  | 0
|  | k |  | Makeline SS sink with fastener | Each | 1 |  | 0
|  | l |  | Loading/Unloading of truck (Domino's material/equipment) | Nos | 2 |  | 0
|  | m |  | Loading/Unloading & disposable of debris (per truck) | Nos | 2 |  | 0
|  | n |  | Loading / Unloading of Servo | Nos | 1 |  | 0
|  | o |  | Water dispenser connection with fittings | Each | 1 |  | 0
|  | q |  | P/F Door Stopper for Makeline /Slap Table | Each | 6 |  | 0
|  | r |  | Fixing Wall Shelf above Slap Table /Sink | Each | 2 |  | 0
|  | s |  | Fixing of Tissue Paper Holder /Helmet Stand | Each | 4 |  | 0
|  | t |  | L.T Panel commisioning as per site requirement | Each | 1 |  | 0
|  | u |  | Servo connections as per site requirement | Each | 1 |  | 0
|  | v |  | Housekeeping | Sqft | RO |  | 0
|  | w |  | Installation of Fresh air and Exhaust Unit | Each | RO |  | 0
|  | y |  | Bike Fixing with providing nutbolt and labour charge | Each | RO |  | 0
|  | ac |  | Fixing of Light Fixtures Provided by JFL (Hood lights are in hood vendor scope) | Each | 59 |  | 0
|  | ae |  | Supplying and erecting double pole metal clad switch with fuse and neutral link 240V, 25A on iron / GI frame switch socket with ISI mark approved make duly erected with modular box , cover plate & all wiring connections complete. (Single phase) | Each | 11 |  | 0
|  | ah |  | OGT Installation with all required plumbing fittings (CPVC) pipe of 32mm dia under three sink unit | Each | 1