## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
A | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
A.1 | Supply, installation and testing of Galvanized Steel / Galvanized Iron, factory fabricated square / rectangular ducts, complete with TDF flanges and bracing necessary supports using thread roads and anchor bolts, supply air collars, vanes, splitters dampers. The ducts shall be fabricated and installed in line with SMACNA standards. (for Supply Air Duct)
A.1.1 | 24 Gauge (for low pressure duct with duct size larger side 0 - 1000 mm) | Sq.Mtr | 40
B | AIR DISTRIBUTION DUCT INSULATION & LINNING
B.1 | Supply, installation & testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with silver foil covering, Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476 with necessary adhesives.
B.1.1 | 19 mm thicknesses | Sq.Mtr | 40
C | AIR DISTRIBUTION DUCT ACCESSORIES
C.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
C.1.1 | Size - 450 x 150 mm | Nos | 4
C.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Opposed Blade Damper / Collar Damper with Nylon gears and lever on face side for smooth operation.
C.2.1 | Size - 450 x 150 mm | Nos |  |  | Ro
D | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
D.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Grille with fixed Aerofoil Blades, with 30° deflection - 2 Way with rigid frame of 16mm flange as standard.
D.1.1 | Neck Size - 450 x 150 mm | Nos | 4
E | TESTING & COMMISIONING
E.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1
E.2 | Supply, installation, testing and commissioning of VAV, fire dampers, control wiring connections etc complete as per design drawings. ( AHU units to be supplied by the client and tap off for the proposed area shall be considered from Existing Duct work as mentioned in the design drawings). | Lot | 1
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.