## F-F-025_ELEC BOQ
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | F-F-025_CS_HYDERABAD AIRPORT |  |  | DATE: | 2024-03-22
|  |  |  | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
Item Code | Item Name | UOM | Qty | UNIT COST | REMARKS
A | METER / METER PANEL
A.1 | Supply, Installation, Testing & Commissioning of Energy Meter / Meter Panel (Prepaid Type) complete with Enclosure (If required as per site condition / Airport TDM). Make / Brand selection as per Airport TDM listed.
A.1.1 | 32A/5A ENERGY METER (CT TYPE) | Nos. | 1
B | LV CABLING
B.1 | Supply, Installation, Testing & Commissioning of Fire Rated LSH / LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground / on Cable Tray / in Pipe / on Wall / Trench as required. For cables laid on Cable Tray / in Pipe / on Wall / Trench - the rate shall include necessary supporting / clamping arrangements.
B.1.1 | 4C x 25 MM2 | Mtr. | LUMP SUM
B.1.2 | 4C x 16 MM2 | Mtr. | LUMP SUM
B.1.3 | 4C x 6 MM2 | Mtr. | LUMP SUM
B.1.4 | 4C x 4 MM2 | Mtr. | LUMP SUM
B.1.5 | 2C x 4 MM2 | Mtr. | LUMP SUM
C | DISTRIBUTION BOARDS
C.1 | Supply, Installation, Testing & Commissioning of Surface / Flush mounting 10kA / 25kA (As per Panel requirement) Phase segregated Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on fork type Insulator, Independent neutral busbar for each phase including inter connecting wiring & earth bus on insulation mount. Make / Brand selection as per Airport TDM listed. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall be Hpi / Si series & MCB's shall be 'B" / 'C' Curve (As per requirement).
LPDB
C.1.2 | 8 Way TPN Panel Board with 32A 4P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. Make / Brand selection as per Airport TDM listed. | Nos. | 1
UPS DB
C.1.3 | 6 Way SPN Panel Board with 20A 2P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. Make / Brand selection as per Airport TDM listed. | Nos. | RO
D | CIRCUIT MAINS & EARTH
D.1 | Supply, Installation, Testing & Commissioning of Sub / Circuit Mains & Earth wires with Fire Rated LSH / LSZH PVC insulated Flexible Copper Wires 660 / 1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back Boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires, etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension. Circuit mains shall be measured from DB to switch board, looping between switch board to outlets / lights, and looping from switch board to switch board.
D.1.1 | 1C x 4 MM2 | Mtr. | LUMP SUM
D.1.2 | 1C x 2.5 MM2 | Mtr. | LUMP SUM
D.1.3 | 1C x 1.5 MM2 | Mtr. | LUMP SUM
E | LIGHT FIXTURES POINT WIRING
E.1 | Supply, Installation, Testing & Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with Lamps, Ballasts / Drivers / Starters, Switches / Lighting Control Switch Board with Fire Rated LSH / LSZH PVC insulated Flexible Copper Wires 660 / 1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make / Brand selection by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
E.1.1 | HANGING LIGHT (Point Wiring only) | Nos. | 5
E.1.2 | DOWN LIGHT COB LIGHT (Point Wiring only) | Nos. | 10
E.1.3 | SIGNAGE LIGHTS (Point Wiring only) | Nos. | 1
E.1.4 | Lighting Control Switch board with switches as required (Point Wiring only) | Nos. | 1
E.1.5 | EXIT LIGHT (Wall / Ceiling Mounted) | Nos. | 2
F | WIRING DEVICES (SWITCHES & SOCKETS)
F.1 | Supply, Installation, Testing & Commissioning of Wiring Devices (Switches & Sockets - Face Plate Finish as approved by Architect / Matching to Architecture Finishes) with Fire Rated LSH / LSZH PVC insulated Flexible Copper Wires 660 / 1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make / Brand selection as per Airport TDM listed / by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
F.1.1 | 6/16A SINGLE SWITCHED SOCKET OUTLET (SYSTEM SOCKETS) | Nos. | 3
F.1.1 | 16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 20
F.1.2 | 20A SINGLE SWITCHED SOCKET OUTLE | Nos. | RO
F.1.3 | 20A SINGLE SWITCHED SOCKET OUTLET (METAL CLAD) | Nos. | RO
F.1.4 | 13A SINGLE SWITCHED UNIVERSAL SOCKET OUTLET + USB PORT | Nos. | RO
F.1.5 | 13A DUAL SWITCHED SOCKET OUTLET | Nos. | RO
F.1.6 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | RO
F.1.7 | 20A DOUBLE POLE SWITCH WITH NEON INDICATOR | Nos. | RO
F.1.8 | BLANK PLATE | Nos. | LMPSUM
F.1.9 | 32A TPN ISOLATOR | Nos. | 1
F.1.10 | DOL STARTER (5HP) | Nos. | RO
G | CONTAINMENT (CABLE TRAY, TRUNKING, CONDUITS)
G.1 | Supply & Installation of GI Cable Tray, GI Cable Trunking, GI / Heavy Duty PVC conduits through wall / ceiling / floor as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc. Make / Brand selection as per Airport TDM listed / by Client.
G.1.1 | 50 x 50 MM CABLE TRUNKING | Mtr. | RO
G.1.2 | 25 MM GI CONDUIT | Mtr. | LUMP SUM
G.1.3 | 20 MM PVC CONDUIT | Mtr. | LUMP SUM
G.1.4 | 25 MM PVC CONDUIT | Mtr. | LUMP SUM
G.1.5 | 32 MM PVC CONDUIT | Mtr. | LUMP SUM
H | UPS SYSTEM
H.1 | Supply, Installation, Testing & Commisioning of 1KVA Single phase UPS with 90 Minute Back-up with SMF Battery Bank + Battery Stand. | Nos. | RO
I | CCTV SYSTEM
I.1 | Supply, Installation, Testing & Commissioning of CCTV System with required cabling through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console / DVR, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make / Brand selection as per Airport TDM listed / by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
I.1.1 | CCTV Dome POS 360 DEGREE Camera, 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. | Nos. | 3
I.1.2 | CCTV IP Dome Camera (CAT 6), 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67 with all neccessary accessories, Power supply units etc. | Nos. | RO
I.1.3 | DVR with 45 Days Back-up | Nos. | 1
I.1.4 | RG 6 Grade 75 Ohm's Co-Axial Cable | Mtr. | LUMP SUM
J | DATA NETWORK SYSTEM
J.1 | Supply, Installation, Testing & Commissioning of Data & Telephone Network System with required cabling through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make / Brand selection as per Airport TDM listed / by Client. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
J.1.1 | Dual Data outlet (RJ45) Jack | Nos. | 1
J.1.2 | Single Data outlet (RJ45) | Nos. | 1
J.1.3 | Patch Cords (1.5 meters length) | Nos. | 2
J.1.4 | CAT 6 Cable | Mtr. | LUMP SUM
GRAND TOTAL NET
NOTE : The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.