## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
AC EQUIPMENT (CHILLED WATER - TYPE)
B.1 | Supply, installation, testing and commissioning of chilled water type High static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3/G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping. The unit shall be suitable for 230 ± 10 volts, 50 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level.
B.1.1 | 3.5 TR - (1300 CFM @ 50-70 PASCAL -ESP) | Nos | 1
VENTILATION FANS
B.2 | Supply, Installation, Testing & commissioning of 25mm thick mineral wool insulated Double Skin Inline fresh air fans (With Pre-Fiter). Outer skin shall be 0.6 mm pre plasticized or powder coated GSS sheet. Inner sheet shall be 0.6 mm plain GSS perforated. Extruded Aluminum corners. Complete with Glass view panel, motor guard, marine light, limit switch, cable entry, GSS base frame. Screw less construction with zero leakage in the panel joints. Inspection door for all the sections. Fan: PLUG TYPE , IE - 3, Motor shall be suitable for Variable Frequency Drive along with control panel and necessary cabling. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Terminal box of the unit shall be IP54 rated. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan. Note : External Static Pressure (ESP) is calculated based on design drawing how ever contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.2.1 | 3300 CFM @ 250 PASCAL - ESP. | Nos | 1
B.3 | Supply, Installation, Testing & Commissioning of Kitchen exhaust air Vane/Tube Axial flow type fans of approved make complete with aluminum alloy blades with aerofoil design, bird screen, flexible connection & gravity louvers at outlet. Motor shall be of IE 3, Motor shall be suitable for Variable Frequency Drive along with control panel and necessary cabling, the motor should be located outside of the hot air stream, Class H insulation. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Sound level at 3 mtr distance from fan outlet shall not be more than 80 db(A).Including control panel and all necessary cabling and terminations. Fans should be AMCA certified for Air & Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3: 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make/model of motor should be supplied by the fan manufacture at the site. RPM Should Not exceed 1450. However lower cfm up to 5000 CFM can be provided at 2850 RPM. Outlet velocity should not exceed 16 m/s. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note : External Static Pressure (ESP) is calculated based on design drawing how ever contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.3.1 | 4130 CFM @ 600 PASCAL - ESP. | Nos | 1
AIR CLEANING EQUIPMENTS
B.4 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry scrubber of approved make with minimum 25 mm thick mineral whool panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate . The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above.
B.4.1 | 4130 CFM | Nos | 1