## HVAC
BILL OF QUANTITIES
PROJECT: | IN-DXN-IDLI.COM (FOOD MAHAL) | [5 empty] | DATE: | 10.12.2024
[7 empty] | REV: | R0
HVAC SERVICE - BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Provisional Sum
B | HVAC EQUIPMENTS
AC EQUIPMENT (CHILLED WATER - TYPE)
B.1 | Supply, installation, testing and commissioning of chilled water type High static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3/G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping. The unit shall be suitable for 230 ± 10 volts, 50 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level.
B.1.1 | 3.5 TR - (1300 CFM @ 50-70 PASCAL -ESP) | Nos | 1 |  | 0 |  | 0 | 0
VENTILATION FANS
B.2 | Supply, Installation, Testing & commissioning of 25mm thick mineral wool insulated Double Skin Inline fresh air fans (With Pre-Fiter). Outer skin shall be 0.6 mm pre plasticized or powder coated GSS sheet. Inner sheet shall be 0.6 mm plain GSS perforated. Extruded Aluminum corners. Complete with Glass view panel, motor guard, marine light, limit switch, cable entry, GSS base frame. Screw less construction with zero leakage in the panel joints. Inspection door for all the sections. Fan: PLUG TYPE , IE - 3, Motor shall be suitable for Variable Frequency Drive along with control panel and necessary cabling. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Terminal box of the unit shall be IP54 rated. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan. Note : External Static Pressure (ESP) is calculated based on design drawing how ever contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.2.1 | 3300 CFM @ 250 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
B.3 | Supply, Installation, Testing & Commissioning of Kitchen exhaust air Vane/Tube Axial flow type fans of approved make complete with aluminum alloy blades with aerofoil design, bird screen, flexible connection & gravity louvers at outlet. Motor shall be of IE 3, Motor shall be suitable for Variable Frequency Drive along with control panel and necessary cabling, the motor should be located outside of the hot air stream, Class H insulation. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Sound level at 3 mtr distance from fan outlet shall not be more than 80 db(A).Including control panel and all necessary cabling and terminations. Fans should be AMCA certified for Air & Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3: 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make/model of motor should be supplied by the fan manufacture at the site. RPM Should Not exceed 1450. However lower cfm up to 5000 CFM can be provided at 2850 RPM. Outlet velocity should not exceed 16 m/s. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note : External Static Pressure (ESP) is calculated based on design drawing how ever contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.3.1 | 4130 CFM @ 600 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
AIR CLEANING EQUIPMENTS
B.4 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry scrubber of approved make with minimum 25 mm thick mineral whool panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate . The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above.
B.4.1 | 4130 CFM | Nos | 1 |  | 0 |  | 0 | 0
C | AC PIPING AND ACCESSORIES
AC CONDENSATE DRAIN PIPE
C.1 | Supply, installation and testing of Rigid uPVC condensate drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape.
C.1.1 | 25 mm Ø | Mtr | 4 |  | 0 |  | 0 | 0
AC CHILLED WATER PIPING
C.2 | Supply, installation and testing of MS class (C) Chilled water pipes with insulation of approved make with vapor barrier and finished with protective coating (Pidilite/Equivalent) over a layer of 7 Mil glass cloth for mechanical protection complete with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports etc. Piping insulation shall be expanded polyurethane foam with 36 kg/m3 minimum density, thickness as specified below, 85% minimum closed cell content and thermal conductivity of 0.019 W/m.k at 10°C. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works.
C.2.1 | 32 mm Ø - (Insulation - 30 mm thick) | Nos | 6 |  | 0 |  | 0 | 0
D | AC PIPING VALVES & ACCESSORIES
D.1 | Supply, installation, testing & Commissioning of FCU Valve Kit of approved make for HVAC fan coil units in heating/cooling systems for FCUs. Complete with pressure independent control valve with proportional linear actuator (Modulating type), three-way shut-off valves, integrated by-pass, Venturi device with pressure test ports , Shut Off valve with Strainer and pre-formed shell insulation made of PPE. Flexible connector with threaded nuts/clamps to be provided between the unit and kit of suitable length.
D.1.1 | 32 mm Ø | Nos | 1 |  | 0 |  | 0 | 0
D.2 | Supply, Installation, Testing, and Commissioning Forged Brass Ball Valve of approved make with full bore lever operated with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled/hot water pipe insulation with threaded connection ends with all necessary fixing arrangements.
D.2.1 | 32 mm Ø | Nos | 2 |  | 0 |  | 0 | 0
D.3 | Supply, Installation, Testing, and Commissioning BTU Meter of approved make with direct pipe connection type or operated via sensor module connected supply and return pipe with all necessary fixing and valve arrangements. LCD display (shows all water parameters), with flow rate, temperature inputs, data storage up to 365 days. The display panel shall be mounted at readable height and it shall include interconnecting wiring between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box with all necessary fixing arrangements. Unit shall be compatible with facility Building Management System. (Make and model shall be as per Airport requirement)
D.3.1 | 32 mm Ø | Nos | 1 |  | 0 |  | 0 | 0
D.4 | Supply, Installation, Testing, and Commissioning of Forged Brass Drain Valve / Drain Cock, of approved make rubber seal, O rings e with all necessary fixing arrangements.
D.4.1 | Drain Valve connected in chilled water supply & return line | Nos | 2 |  | 0 |  | 0 | 0
D.5 | Supply, Installation, Testing, and Commissioning of Forged Brass Automatic Air Vent of approved make with all necessary fixing arrangements.
D.5.1 | Automatic Air Vent connected in chilled water supply & return line | Nos | 2 |  | 0 |  | 0 | 0
D.6 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements.
D.6.1 | Dial Size - 63 mm Ø | Nos | 2 |  | 0 |  | 0 | 0
D.7 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements.
D.7.1 | Dial Size - 63 mm Ø | Nos | 2 |  | 0 |  | 0 | 0
D.8 | Supply, installation, testing & commissioning of Test point of approved make with all necessary fixing arrangements..
D.8.1 | Test point for supply and return lines | Nos | 2 |  | 0 |  | 0 | 0
E | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
E.1 | Supply, installation and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square / Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
E.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 14 |  | 0 |  | 0 | 0
E.1.2 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.mtr | 29 |  | 0 |  | 0 | 0
E.2 | Supply, installation, and testing of Black Steel (BS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
E.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 26 |  | 0 |  | 0 | 0
FLEXIBLE DUCTS
E.3 | Supply, installation, and testing of Insulated Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by air handling units or any other equipment's connected to the duct with air tight fittings with all necessary accessories.
E.3.1 | For FCU | Nos | 1 |  | 0 |  | 0 | 0
F | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS & ACCOUSTIC LINNINGS
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
F.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6: 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg/m.s.Pa i.e. μ>7000: Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 / EN 12086 & EN13469. Black Colour with having a density of 50 ± 10 Kg/M3. Quote shall be inclusive of necessary Adhesive.
F.1.2 | 13 mm thicknesses - (SAD) | Sq.mtr | 14 |  | 0 |  | 0 | 0
F.1.2 | 25 mm thicknesses - (FAD) | Sq.mtr | 29 |  | 0 |  | 0 | 0
F.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using rockwool with silver foil covering, density of 50 Kg/m3.Quoute shall be inclusive of necessary Adhesive.
F.2.1 | 25 mm thicknesses - (KEAD) - For Kitchen Exhaust | Sq.mtr | 26 |  | 0 |  | 0 | 0
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
F.3 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg/m3 Quote shall be inclusive of necessary Adhesive. Thermal conductivity of the insulation material shall not exceed 0.047 W/m K at an average temperature of 20°C.
F.3.1 | 15 mm thicknesses - (SAD) | Sq.mtr | 4 |  | 0 |  | 0 | 0
G | AIR DISTRIBUTION DUCT - DAMPERS
DUCT AIR CONTROL DAMPERS
G.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper / Collar Damper of approved make.
G.1.1 | Size - 300 x 300 mm | Nos | 4 |  | 0 |  | 0 | 0
G.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
G.2.1 | Size - 250 x 150 mm | Nos | 7 |  | 0 |  | 0 | 0
G.2.2 | Size - 300 x 150 mm | Nos | 1 |  | 0 |  | 0 | 0
G.2.3 | Size - 350 x 300 mm | Nos | 1 |  | 0 |  | 0 | 0
G.2.4 | Size - 400 x 200 mm | Nos | 1 |  | 0 |  | 0 | 0
G.2.5 | Size - 400 x 350 mm | Nos | 1 |  | 0 |  | 0 | 0
G.2.6 | Size - 500 x 450 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.(For Kitchen Exhaust MS duct)
G.3.1 | Size - 250 x 250 mm | Nos | 7 |  | 0 |  | 0 | 0
G.3.2 | Size - 300 x 250 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3.3 | Size - 350 x 300 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3.4 | Size - 600 x 300 mm | Nos | 1 |  | 0 |  | 0 | 0
H | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
H.1 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar / Square Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange frame with 8 mm step suitable to tegular / grid type false ceiling with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.1.1 | Neck Size - 300 mm X 300 mm - (2 - Way) | Nos | 6 |  | 0 |  | 0 | 0
LOUVERS
H.2 | Supply, installation, and testing of Extruded Aluminium Fresh Air Sand Trap Louver of approved make with Bird screen and Wire mesh with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.2.1 | Size - 750 mm X 600 mm | Nos | 1 |  | 0 |  | 0 | 0
H.3 | Supply, installation, testing and commissioning of Extruded Aluminium Exhaust Air Louver of approved make with 45 degree blades to avoid rain water penetrations continued with wire mesh and bird screen, 30 mm flange with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.3.1 | Size - 950 mm X 600 mm | Nos | 1 |  | 0 |  | 0 | 0
J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
J.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
K | TESTING AND BALANCING
K.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates |  |  | Lumpsum
K.2 | Water balancing of Entire Chilled and Hot Water piping system to arrive the designed flow rates. |  |  | Lumpsum
K.3 | Chilled water and Hot water pipe Pressure testing at 15kgf/cm2 hydrostatics pressure for a minimum 24hrs hold time .Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
L | SHOP DRAWINGS & APPROVALS
L.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
M | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
M.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
M.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
M.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
M.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.

## ELEC & ELV
BILL OF QUANTITIES
PROJECT: | IN-DXN-IDLI.COM (FOOD MAHAL) | [5 empty] | DATE: | 2024-12-10
[7 empty] | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire, and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING/ INTEGRATING UNIT M&E SERVICES TO AIRPORT M&E SERVICES/ BUILDING
A.1 | If any termination /connection of the unit services are required outside the site location (i.e. connection of the unit M&E to the airport M&E or service termination to the airport external façade/ roof etc.); then the contractor has to work in consultation with the airport to plan, design & detail for such connections. The contractor to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor to make good after installation any penetrations including providing fire seals as requried as per airport requirement. |  |  | Provisional Sum
B | METER / METER PANEL
B.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). The RYB sequence should be provided. Energy Meter shall be of Digital kVAH Type and compatible with Airport BMS for realtime monitoring, of approved make or any other make with kVAH option with Approval from TS Department.
B.1.1 | 63/5A Energy Meter(Direct)-3 Phase | Nos | 1 |  | 0 |  | 0 | 0
C | LV CABLING
C.1 | Supply and Laying of approved make Fire Rated LSZH XLPE insulated PVC sheathed,AL/ Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & earthing). The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench using necessary supporting / clamping arrangements.The cable shall be provided with cable identification tags made out of Aluminium strip, engraved with cable size and the routing.
C.1.1 | 3.5C x 50 Sq. mm XLPE AL Armoured Cable + 2 x 8 SWG CU. | Mtr | 12 |  | 0 |  | 0 | 0
C.1.2 | 4C x 4 Sq. mm XLPE CU. Armoured Cable + 10 SWG CU. | Mtr | 12 |  | 0 |  | 0 | 0
D | CABLE END TERMINATIONS
D.1 | Supply and Installation of approved make cable end Termination for the following cables using Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing of adequate size, etc.complete.
D.1.1 | 3.5C x 50 Sq. mm XLP Al. Armoured Cable | Nos | 4 |  | 0 |  | 0 | 0
D.1.2 | 4C x 4 Sq. mm XLPE CU Armoured Cable | Mtr | 2 |  | 0 |  | 0 | 0
E | DISTRIBUTION BOARDS
E.1 | Supply, Installation, Testing & Commissioning of approved make Surface / Flush / Floor mounting 10kA / 25kA Distribution Boards, Devices, Relays and all accessories. The RYB sequence should be provided at the incomer entry, followed by on/off and trip indicators. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring & earth bus on insulation mount, complete with Protective devices (MCCB, MCB, RCCB, RCBO, etc.) The Contractor shall be responsible to supply materials and equipment complying with the green building specification if required. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Locations. The RCCB / RCBO shall be Hpi / Si series & MCB's shall be 'B" / 'C' Curve (As per Airport requirement).
E.1.1 | LPDB-02 | Each | 1 |  | 0 |  | 0 | 0
12 Way Three phase Panel board
Incomer
100A TP MCCB - 1 No.
Outgoings
10/16/20/25A SP MCB- 33 Nos
25A 4P RCBO 30mA - 1 No.
F | LIGHT POINT WIRING
F.1 | Supply, Installation, Testing & Commissioning of Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with approved makes Switches / Lighting Control Switch Board with FRLSH PVC insulated Flexible Copper Wires 660/1100V grade using 2 X 1.5 Sq mm PVC insulated fine stranded single core FRLSH copper conductor wires phase and neutral and with 1.5 Sq mm PVC insulated, green coloured, fine stranded single core copper cable as earth continuity, earth wire crimped to copper socket, fastened using brass bolt and nut etc through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit.Wiring shall be as per IS 732. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
F.1.1 | 1 No. light point controlled by 1 No 10A, SP Switch. | Nos | 4 |  | 0 |  | 0 | 0
F.1.2 | Secondary light points. (from the first light point without supply and installation of switches.) | Nos | 10 |  | 0 |  | 0 | 0
G | CIRCUIT WIRING
G.1 | Supply, Installation, Testing & Commissioning of approved makes FRLSH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit/ GI Trunking (Containment size & Type selection as per site requirement) for the following types of wires.
G.1.1 | Circuit wiring for light points using 2 Runs of 2.5 sq.mm PVC insulated copper wires along with 1 Run of 1.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit / GI Trunking from DB to Light control switch box/Normal Sockets. | Mtr | 460 |  | 0 |  | 0 | 0
G.1.2 | Power points using 2 Runs of 4 sq.mm PVC insulated copper wires along with 1 Run of 2.5 sqmm pvc copper wire (Green) for continuous earthing, through suitable GI Conduit / GI Trunking from DB to Power points. | Mtr | 220 |  | 0 |  | 0 | 0
H | POWER POINTS (SWITCHES & SOCKETS)
H.1 | Supply, Installation, Testing & Commissioning of approved makes Devices (Switches & Sockets - Face Plate Finish as approved by Architect / Matching to Architecture/interior Finishes) complete with suitable GI Back boxes, Earthing, accessories, glands, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. on Surface / Concealed as per site condition & maintain aesthetic of the unit.Type annd IP rating should be as per Airport requirements. The rate shall include wall chasing, chipping of floors, rough plastering. The unit shall be suitable for 400 ± 15 volts 3 phase and 230 ± 10 volts 1 phase, 50/60 Hz, AC supply as per Airport / Country power supply.
H.1.1 | 13A Single Switched Socket Outlet | Nos | 24 |  | 0 |  | 0 | 0
H.1.2 | 13A Dual Switched Socket Outlet | Nos | 2 |  | 0 |  | 0 | 0
H.1.3 | 16A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) | Nos | 3 |  | 0 |  | 0 | 0
H.1.4 | 20A Single Phase Industrial Switched Socket (3 Pin) (Wall Mounted Metal Clad Socket) | Nos | 5 |  | 0 |  | 0 | 0
H.1.5 | 20A Unswitched Fused Connection Outlet with-out Neon Indicator. | Nos | 3 |  | 0 |  | 0 | 0
H.1.6 | 20A Double Pole Switch with Neon indicator | Nos | 3 |  | 0 |  | 0 | 0
H.1.7 | 25A Three Phase Industrial Switched Socket (5 Pin) (Wall Mounted Metal Clad Socket) | Nos. | 1 |  | 0 |  | 0 | 0
H.1.8 | 20A Isolator with suitable metal enclosure | Nos. | 2 |  | 0 |  | 0 | 0
H.1.9 | One Gang Blank Plate | Nos | 2 |  | 0 |  | 0 | 0
J | LIGHTING FIXTURES
J.1 | Supply, Installation, testing and commissioning of approved makes Light fixtures complete with accessories. Rate shall include necessary mounting bracket, suspension chains etc.
J.1.2 | Exit Light (Wall / Ceiling Mounted) | Nos | 1 |  | 0 |  | 0 | 0
K | CONTAINMENT
K.1 | Supply & Installation of approved makes medium duty Hot dip perforated GI Cable Tray, through Wall / Ceiling as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc.
K.1.1 | 200 x 50 mm Cable Tray | Mtr. | 5 |  | 0 |  | 0 | 0
K.1.2 | 100 x 50 mm Cable Tray | Mtr. | 10 |  | 0 |  | 0 | 0
L | CCTV SYSTEM
L.1 | Supply, Installation, Testing & Commissioning of approved makes CCTV System with suitable / required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console DVR with Power Box , Suitable POE with Port switch & Surveillance hard disk,etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
L.1.1 | CCTV ceiling Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. | Nos | 2 |  | 0 |  | 0 | 0
L.1.2 | CCTV wall Mount Dome Camera, As approved or confirmed by client with all neccessary accessories, etc. | Nos | 1 |  | 0 |  | 0 | 0
L.1.3 | SITC of CAT6 cable on surface /concealed/ wall, including suitable conduits, fittings, accessories, etc. | Mtr. | 100 |  | 0 |  | 0 | 0
M | DATA NETWORK SYSTEM
M.1 | Supply, Installation, Testing & Commissioning of approved makes Data & Telephone Network System with required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF/SERVER Rack using patch cordes, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
M.1.1 | Single Data outlet (RJ45) Jack | Nos | 2 |  | 0 |  | 0 | 0
M.1.2 | Dual Data outlet (RJ45) Jack | Nos | 1 |  | 0 |  | 0 | 0
M.1.3 | Wi-Fi Router | Nos | 1
M.1.4 | SITC of CAT6 cable on surface /concealed/ wall, including suitable conduits, fittings, accessories, etc.(For dummy points cabling considered) | Mtr. | 125 |  | 0 |  | 0 | 0
N | PA SYSTEM
N.1 | Supply, Installation, Testing & Commissioning of approved makes PA System with required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI back boxes, Earthing, EOLR, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
N.1.1 | 6 Watts ceiling mount Speaker with all the necessary accessories | Nos | 1 |  | 0 |  | 0 | 0
N.1.2 | Volume Controller | Nos | 1 |  | 0 |  | 0 | 0
N.1.3 | SITC of 2C 1.5 Sq mm Cu multi-stranded PVC insulated shielded FRLS cable | Mtr. | 40 |  | 0 |  | 0 | 0
O | ELECTRICAL SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
O.1 | All services like Panels, Cables, Pipes etc need to be clearly labelled or tagged at site with service identification, direction etc. And all equipment needs to tagged as per Airport requirements.
O.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
P | MISCELLANEOUS
P.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
P.1.1 | Providing and Fixing of Electrical Standard Grade Rubber Mat suitable for LT Volts | Unit | 1 |  | 0 |  | 0 | 0
P.1.2 | Provide and Fixing Shock Treatment Chart | Unit | 1 |  | 0 |  | 0 | 0
P.1.3 | Provide and Fixing of L.T. danger sign boards in Panel side | Unit | 1 |  | 0 |  | 0 | 0
Q | SHOP DRAWINGS & APPROVALS
Q.1 | Preparation and submission of a detailed shop drawing for the electrical system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, plumbing, and fire services, along with updating SLD, load calculation sheets, and power layouts as per approved, selected, or supplied equipment power and phase requirements, this also needs to be coordinated with latest architectural, structural and interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
R | ANY ADDITIONAL ITEMS
R.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
R.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit |  |  | 0 |  | 0 | 0
R.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit |  |  | 0 |  | 0 | 0
R.1.3 | Item 2 - (Contractor to describe only if there are any) | Unit |  |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.

## PLUMBING
BILL OF QUANTITIES
PROJECT: | IN-DXN-IDLI.COM (FOOD MAHAL) | [5 empty] | DATE: | 2024-12-10
[7 empty] | REV: | R0
PLUMBING SERVICE - WORKS BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (XX) | (XX) | (XX) | (XX) | (XX)
A | CONNECTING / INTEGRATING UNIT M&E SERVICES TO AIRPORT M&E SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Provisional Sum
B | DRAINAGE & VENT SYSTEMS
DRAINAGE EQUIPMENTS
B.1 | Supply, Installation and Testing of Grease Trap (Above Ground/floor) of approved make of 304-grade stainless steel material with interceptor body, perforated bucket, baffles, integral trap, inlet, and outlet pipe sleeve, and stainless steel interceptor cover with all necessary fittings & connectors, etc.
B.1.1 | 8 GPM - Flow Rate (0.50 LPS / 30.28 LPM) | Nos | 2 |  | 0 |  | 0 | 0
VALVES & ACCESSORIES
B.2 | Supply, Installation and Testing of Air Admittance Valve of approved make conforming to EN 12380, with an air admittance air flow rate of 6.1 LPS and a temperature range of operation from -20 ˚C to + 60 ˚C with all necessary adapters, fittings and connectors etc.
B.2.1 | 32 mm Dia | Nos | 2 |  | 0 |  | 0 | 0
DRAINS, TRAPS & CLEANOUTS
B.3 | Supply, Installation and Testing of AISI 304 grade Stainless Steel Floor Drain of approved make with top square anti-slip mesh grating drain cover of 300 X 300 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap with all necessary adapters, fittings and connectors etc.
B.3.1 | 50 mm Dia - Outlet | Nos | 2 |  | 0 |  | 0 | 0
B.4 | Supply, Installation and Testing of uPVC Multi Floor Trap of approved make with stainless steel slotted top cover, flap, and air-tight cleaning eye, odor water seal trap with all necessary adapters, fittings, and connectors, etc.
B.4.1 | ( 3 Nos X 50 mm Dia - Inlet ) 75 mm Dia - Outlet | Nos | 1 |  | 0 |  | 0 | 0
B.5 | Supply, Installation and Testing of of uPVC 'P' Trap (self-cleaning type) of approved make with odor water seal trap with all necessary adapters, fittings and connectors, etc.
B.5.1 | 40 mm Dia - Outlet | Nos | 3 |  | 0 |  | 0 | 0
DRAINAGE & VENT SYSTEMS PIPING
B.6 | Supply, Installation and Testing of of uPVC Pipe of approved make conforming to IS 13592, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements.
B.6.1 | 32 mm Dia | Nos | 2 |  | 0 |  | 0 | 0
B.6.2 | 40 mm Dia | Nos | 5 |  | 0 |  | 0 | 0
B.6.3 | 50 mm Dia | Nos | 17 |  | 0 |  | 0 | 0
B.6.4 | 75 mm Dia | Nos | 2 |  | 0 |  | 0 | 0
TESTING & COMMISSIONING
B.8 | Water / Air Test for Drainage and Vent system pipes for leak detection
B.8.1 | The drainage and vent system shall be water/air tested with all openings in the piping tightly closed, except the highest opening to detect any water leakage in the system. The test is to be conducted after the complete installation of all drainage and vent system pipes and accessories as per the proposed design. | Set | 1 | Lumpsum
C | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
C.1 | Supply, Installation, Testing, and commissioning of Electric Water Heater of approved make with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. The unit shall be suitable for 230 ± 10 volts, 50/60 Hz, 1 phase AC supply and proper supports necessary as per standards and site condition/requirements.
C.1.1 | 40 Litres vertical storage water heater | Nos | 1 |  | 0 |  | 0 | 0
C.2 | Supply, Installation, Testing of Multi-Jet water meter of approved make conforming to IS: 779/94 and Class B of ISO: 4064, with Brass body and coupling, hermetically sealed water meter with magnetically driven totalizer, sealed against tampering, leakproof having dry dial, etc. and shall be operated with a working condition of water temperature upto 50°C and a Maximum pressure of 16 Bar( with BMS integration ).
C.2.1 | 25 mm Dia | Nos | 1 |  | 0 |  | 0 | 0
C.3 | Supply, Installation, Testing, and commissioning of RO Filter with inbuild pump of approved make of compact size for supplying pure filtered potable water to equipment like Combi-steamers & and baking ovens, Fresh water taps and coolers, Coffee/ Espresso machines, Post-mix machines, Ice-machines, and Boiling-water taps etc. with Indicating panel, Dust proof cover, filter cartridges, Pressure pump, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. The final make, model, and details are to be finalized by the specialist vendor after examining the water test report of the incoming water supply provided at the site.
C.3.1 | 1.5 Ltrs / Min - Flow Rate | Nos | 1 |  | 0 |  | 0 | 0
TAPS
C.4 | Supply, Installation, Testing, and Commissioning of chrome plated Mixer Tap with Flexible hose connector, Pillar tap fixing studs, Washer etc.. with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards.(Model as per Equipment ventor/ID Design/Architectural design)
C.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 3 |  | 0 |  | 0 | 0
WATER SUPPLY PIPE VALVES & ACCESSORIES
C.6 | Supply, Installation and Testing of Brass Ball Valve of approved make with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar with all necessary fittings.
C.6.1 | 25 mm Dia | Nos | 3 |  | 0 |  | 0 | 0
C.7 | Supply, Installation and Testing of chrome plated Angle Valve of approved make with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards.
C.7.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 8 |  | 0 |  | 0 | 0
C.7.2 | 20 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 4 |  | 0 |  | 0 | 0
C.8 | Supply, Installation and Testing of Water Hammer Arrester of approved make with Factory air charged and permanently sealed for an Air pre-load of 4.2 Bar, Designed to operate at a working pressure of 10.6 Bar, and temperature range of 0.5°C to 82°C with all necessary fittings & connectors etc.
C.14.1 | 25 mm Inlet Dia | Nos | 1 |  | 0 |  | 0 | 0
COLD WATER SUPPLY PIPING
C.9 | Supply, Installation and Testing of (Chlorinated Poly Vinyl Chloride) CPVC Pipe of approved make conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions, etc, and proper supports were necessary as per standards and site condition/requirements.
C.9.1 | 15 mm Dia | Mtr | 5 |  | 0 |  | 0 | 0
C.9.2 | 20 mm Dia | Mtr | 10 |  | 0 |  | 0 | 0
C.9.3 | 25 mm Dia | Mtr | 12 |  | 0 |  | 0 | 0
HOT WATER SUPPLY / RETURN PIPING
C.10 | Supply, Installation and Testing of (Chlorinated Poly Vinyl Chloride) CPVC Pipe of approved make conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 85°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions, etc, and proper supports were necessary as per standards and site condition/requirements.
C.10.1 | 15 mm Dia | Mtr | 4 |  | 0 |  | 0 | 0
C.10.2 | 20 mm Dia | Mtr | 5 |  | 0 |  | 0 | 0
PIPING THERMAL INSULATION
C.11 | Supply and fixing of Pipe Insulation of 9 mm thick, with closed cell flexible elastomeric foam made from Nitrile rubber with 26-gauge Aluminium cladding of approved make to prevent external mechanical damage of approved make for Hot water pipe with an operating temperature range of -40°C to +105°C, Thermal conductivity (λ) 0.040 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe.
C.11.1 | For 15 mm Pipe Dia | Mtr | 4 |  | 0 |  | 0 | 0
C.11.2 | For 20 mm Pipe Dia | Mtr | 5 |  | 0 |  | 0 | 0
D | PLUMBING SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
D.1 | All services for pipes Like Type of water, pipe size, Flow direction need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
D.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1
E | TESTING & COMMISSIONING
E.1 | Water Quality Analysis Report
E.1.1 | Supplied incoming water samples are to be tested for pH value, Conductivity, TDS, Total Hardness, Mineral contents, Total Chlorine, Bacteria presence, color, odor, etc. to identify whether the supplied water is suitable for drinking purposes and also to finalize the selection/design of water filtration/treatment system. The test/analysis is to be conducted before any construction related to the water supply system at the site. | Set | 1 | Lumpsum
E.2 | Incoming water supply tap-off point water pressure and flow test
E.2.1 | Incoming water supply tap-off point water pressure is to be tested at the site to identify whether the water supply has sufficient pressure and flow to serve the remote end plumbing fixture/equipment with minimum flow pressure requirement to the fixture. (The proposed water supply design is based on the assumption that the supplied water has enough pressure and flow to serve the plumbing fixtures/equipment). The test is to be conducted prior to any construction related to the water supply system at the site. | Set | 1 | Lumpsum
E.3 | Pressure test for Water supply system pipes for leak detection
E.3.1 | Water supply system pipes are to be pressure tested at the site with a Test pressure / Head of 10 Bar for a duration of 24 Hours to detect any water leakage in the system. The test is to be conducted after the complete installation of all water supply system pipes and accessories as per the proposed design. | Set | 1 | Lumpsum
F | SHOP DRAWINGS & APPROVALS - DRAINAGE & WATER SUPPLY
F.1 | Preparation and submission of a detailed shop drawing for the Plumbing system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, Electrical, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
G | MISCELLANEOUS OR ANY ADDITIONAL ITEMS - DRAINAGE & WATER SUPPLY
G.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
G.1.1 | Item 1 - (Contractor to describe only if there are any) |  |  |  | 0 |  | 0 | 0
G.1.2 | Item 2 - (Contractor to describe only if there are any) |  |  |  | 0 |  | 0 | 0
G.1.3 | Item 3 - (Contractor to describe only if there are any) |  |  |  | 0 |  | 0 | 0
GRAND TOTAL
Note : The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at site and provide the quantity and cost over and above this BOQ. Any service penetration is to be made good after installation. Fire sealing is to be done for penetrations as per site requirements.

## GAS
BILL OF QUANTITIES
PROJECT: | IN-DXN-IDLI.COM (FOOD MAHAL) | [5 empty] | DATE: | 10.12.2024
[7 empty] | REV: | R0
GAS SERVICES - BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (XX) | (XX) | (XX) | (XX) | (XX)
A | CONNECTING / INTEGRATING UNIT MandE SERVICES TO AIRPORT MandE SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Provisional Sum
B | GAS SYSTEMS
GAS SUPPLY EQUIPMENTS & METERING
B.1 | Supply, Installation, Testing, and Commissioning of Gas Meter with a maximum pressure range of 0.5 Bar or as per Airport guidelines or standards, operating temperature range of -20°C to +60°C, of approved make and with all necessary fittings and connectors, etc.
B.1.1 | Max flow rate - 10 m3/h | Nos | 1 |  | 0 |  | 0 | 0
GAS SUPPLY PIPE VALVES & ACCESSORIES
B.2 | Supply, Installation, Testing, and Commissioning of Chrome Plated Brass Ball Valve with double O-ring stem, nut with anti-corrosion coating, and steel lever handle with anti-corrosion treatment and PVC coating, suitable for Gas pipe service of approved make and with all necessary fittings and connectors, etc.
B.2.1 | 32 mm Dia | Nos | 3 |  | 0 |  | 0 | 0
B.3 | Supply, Installation, Testing, and Commissioning of Gas Solenoid Valve with manual reset, operating pressure 6 Bar, operating temperature range -15°C to +60°C with a protection class of IP65 of approved make with integration to Gas leak detection, Kitchen Fire suppression systems, and Fire alarm systems as per Airport guidelines or standards requirement and with all necessary fitting and connectors, etc.
B.3.1 | 20 mm Dia | Nos | 2 |  | 0 |  | 0 | 0
B.4 | Supply, Installation, Testing, and Commissioning of Automatic Gas Shutt-off Valve of approved make and with all necessary fitting and connectors
B.4.1 | 25 mm Dia | Nos | 1 |  | 0 |  | 0 | 0
B.5 | Supply, Installation, Testing, and Commissioning of Second Stage Regulator with adjustable pressure control, inlet pressure of 0.5 Bar, and outlet pressure to suit the kitchen equipment of approved make and with all necessary fittings and connectors, etc.
B.5.1 | AS PER EQUIPMENT REQUIREMENTS | Nos | 3 |  | 0 |  | 0 | 0
B.6 | Supply, Installation, Testing, and Commissioning of Pressure Guage with a range of 0 - 30 PSI (0 - 2 Bar) and 63 mm dial size of approved make and with all necessary fittings, isolation valves and connectors, etc.
B.6.1 | 1/4 - inch NPT on bottom Connection | Nos | 2 |  | 0 |  | 0 | 0
GAS SUPPLY PIPING
B.7 | Supply, Installation, Testing, and commissioning of Schedule 40 Carbon Steel Pipe with all necessary fittings such as bends, elbows, tees, reducers, unions, threading, cutting and welding etc. The pipes are to be applied with 2 coats of primer and 2 coats of enamel finish paint of approved color and with proper pipe supports necessary as per standards and site condition/requirements. Complete pipeline to be flushed with Nitrogen before commissioning of the system.
B.7.4 | 20 mm Dia | Mtr | 10 |  | 0 |  | 0 | 0
B.7.5 | 25 mm Dia | Mtr | 7 |  | 0 |  | 0 | 0
B.7.6 | 32 mm Dia | Mtr | 8 |  | 0 |  | 0 | 0
B.8 | Supply, Installation, Testing, and commissioning of Corrugated Stainless Steel Flexible Gas Pipe (CSST) conforming to BS EN 15266 with an operating pressure of 0.5 Bar, UV resistant PVC jacket, and all necessary fittings such as adapters, couplers, tees, nipples, reducers, nuts, washers, gasket, and necessary connections, etc. Proper pipe supports are necessary as per standards and site conditions/requirements.
B.8.1 | 15 mm Dia | Mtr | 3 |  | 0 |  | 0 | 0
C | GAS SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
C.1 | All services for pipes Like Type of Gas, pipe size, Flow direction need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
C.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
D | TESTING & COMMISSIONING
D.1 | Pressure test for Gas supply piping system for leak detection
D.1.1 | Gas piping systems are to be tested at the site with a test pressure three times the working or operating pressure recommended as per airport design guidelines for a holding time period of at least 30 minutes. The test is to be conducted after the complete installation of all gas supply pipes, including all valves and accessories, as per the proposed design. | Set | 1 | Lumpsum
E | SHOP DRAWINGS & APPROVALS
E.1 | Preparation and submission of a detailed shop drawing for the gas piping system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, Electrical, Plumbing, and Fire along with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
F | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
F.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
F.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
F.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
F.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.

## FIRE
BILL OF QUANTITIES
PROJECT: | IN-DXN-IDLI.COM (FOOD MAHAL) | [5 empty] | DATE: | 2024-12-10
[7 empty] | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. | Provisional Sum
B | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
B.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test presure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangement with ceiling / wall etc.
B.1.1 | Pendant type of 68° C (Finishing - Chrome Plated) | Nos | 1
B.1.2 | Pendant type of 79° C (Finishing - Chrome Plated) | Nos | 5
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
B.2 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc.
B.2.1 | 100 mm Dia | Nos | 1
B.3 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions.
B.3.1 | 25 mm Dia | Nos | 1
B.4 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable.
B.4.1 | 100 mm Dia | Nos | 1
B.5 | Supply, Installation, Testing & Commissioning of Pressure Guage with a range of (0 - 300) PSI and 90mm dial size, near to flow switch with ball valves, siphon, fittings like unions/colors/reducer etc.
B.5.1 | Pressure Gauge with 1/4" BSPT / NPT connection | Nos | 1
FIRE SPRINKLER PIPING
B.6 | Supply, Installation, Testing & Commissioning of MS "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns)
B.6.1 | 25 mm Dia | Mtr | 10
B.6.2 | 50 mm Dia | Mtr | 5
B.6.3 | 65 mm Dia | Mtr | 5
B.7 | Supply & Fixing of UL Listed Stainless Steal Braided Flexible Sprinkler Hose with a working pressure of 12 Bar, Inlet Nipple(1" (25mm) BSPT/ NPT connection),Outlet Reducer (1/2" (15mm) BSPT / NPT connection), Isolation Ring, Gasket, Snap Clamp, T-bar bracket (TBL or TBS),Stock bar and Nuts etc.
B.7.1 | Assembly Length of (1500 mm) | Nos | 6
C | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE )
FIRE ALARM SYSTEM - DETECTION DEVICES
C.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke & Heat) Smoke Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles with all necessary mounting and fixing arrangements. (Above & Below Ceiling)
C.1.1 | Above ceiling level | Nos | 1
C.2 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector of approved make conforming by local fire authorities, with standard detector mounting base, IP30 Ingress Protection, suitable area coverage (subject to local standard), 360° Angle Visibility with suitable class approved by LPCB, with all necessary mounting and fixing arrangements.
C.2.1 | Heat Detector - 58°C fixed temperature | Nos | 2 |  | 0 |  | 0 | 0
C.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements.
C.3.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 1
FIRE ALARM SYSTEM - AUDIBLE AND VISUAL NOTIFICATION DEVICES
C.4 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & and operating temp (- 10 degrees to + 55 degrees) complete as required and duly approved by LPCB / EN54 along with suitable size 2 core cable clipped to structure/wall/ceiling / through GI or Heavy Duty PVC Conduits with suitable cable clips/saddles.
C.4.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 1
C.5 | Supply, Installation, Testing, and Commissioning of Addressable Type Response Indicator of approved make conforming by local fire authorities with high bright LED, for Fire Detectors to indicate quickly the source of an alarm signal from detectors, which are not easily accessible or visible with IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) approved by LPCB, with all necessary mounting and fixing arrangements.
C.5.1 | Response Indicator / Remote Indicator | Nos | 1 |  | 0 |  | 0 | 0
FIRE ALARM SYSTEM - MODULE DEVICES
C.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolator Module of approved make to identify the shorted and de-wired detectors and devices in the circuit duly approved by LPCB / EN54, with all necessary mounting, termination and fixing arrangements.
C.6.1 | Isolator Module | Nos | 1 |  | 0 |  | 0 | 0
C.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Monitor Module of approved make for Sprinkler Flow Switch & WLD Monitoring, Address Switch to program the modules, complete duly approved by LPCB / EN54, with all necessary mounting, termination and fixing arrangements.
C.7.1 | Monitor Module | Nos | 2 |  | 0 |  | 0 | 0
FIRE ALARM SYSTEM - CABLING
C.8 | Supply, Installation, Testing and Commissioning FRLS/ FP200 PVC insulated and PVC sheathed armoured multi-stranded Copper conductor of approved make RED coloured cable clipped to structure/wall/ceiling / through approved make GI or Heavy Duty PVC Conduits with suitable cable clips/saddles suitable for flush and surface mounting with all necessary mounting, termination, tap-off connections and fixing arrangements.
C.8.1 | 2C x 1.5 Sq. mm Cu Cable | Mtr | 20 |  | 0 |  | 0 | 0
D | FIRE EXTINGUISHERS
D.1 | DRY POWDER STORED FIRE EXTINGUISHER
D.1.1 | Supply and fixing of 4 KG ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. | Nos | 1
D.2 | CO2 PORTABLE FIRE EXTINGUISHER
D.2.1 | Supply and fixing of 4.5 KG CO2 (Carbon-dioxide type) of approved make Fire Extinguisher. Design, construction and testing as per local Fire Authority Rating, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade, Supplied with standard accessories. | Nos | 2 |  | 0 |  | 0 | 0
D.3 | K CLASS STORED PRESSURE FIRE EXTINGUISHER WITH SS BODY
D.3.1 | Supply and fixing of 6 Ltr Class K wet chemical Type Fire Extinguisher of approved make and as per local Fire authority Rating, Pressurized with nitrogen gas at 10 bar and body Hydrotested at 35 bar, Operating temperature +5°C to +60°C, Supplied with standard accessories. | Nos | 1 |  | 0 |  | 0 | 0
D.4 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
D.4.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality M.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. | Nos | 4
D.10 | FIRE BLANKET
D.10.1 | Supply and fixing of wall mounted Fire Blanket with Fire Blankets of approved make made up of a Fire-retardant material, folded and packaged in a quick-release contraption for easier storage as per local Fire Authority regulations, Supplied with standard accessories. | Nos | 1 |  | 0 |  | 0 | 0
E | KITCHEN EXHAUST HOOD FIRE SUPPRESSION SYSTEM
E.1 | Detail Design, Supply, Installation, Testing & Commissioning of Kitchen Hood Fire Suppression System of approved make should be provided by specialist vendor as per local Fire Authority regulations. Supplied with standard accessories.
E.1.1 | For Kitchen Exhaust Hood | Nos | 2 |  | 0 |  | 0 | 0
F | TESTING AND BALANCING
F.1 | Checking the functionality of all installed devices, conducting alarm tests, verifying proper communication between control panels and devices, and other systems. Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
F.2 | Sprinkler pipe Pressure testing hydrostatic pressure test of no less than 14 bar (200PSI) for 2 hours with zero loss in pressure at the reference gauge or visual observation of a leak. Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
F.3 | Ensure all extinguishers are properly labelled, mounted, and ready for use. Training for staff on correct usage should be included. Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
G | SHOP DRAWINGS & APPROVALS
G.1 | Preparation and submission of a detailed shop drawing for the Fire Detection & Fire Protection systems after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, Electrical and Plumbing, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
H | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
H.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
H.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
H.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
H.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.