## HVAC
BILL OF QUANTITIES
PROJECT: | IN-DXN-BRAJ KI GALIYAN (FOOD MAHAL) | [5 empty] | DATE: | 2024-12-09
[7 empty] | REV: | R0
HVAC SERVICE - BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (XX) | (XX) | (XX) | (XX) | (XX)
A | CONNECTING / INTEGRATING UNIT MEP SERVICES TO AIRPORT MEP SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Provisional Sum
B | HVAC EQUIPMENTS
AC EQUIPMENT (CHILLED WATER - TYPE)
B.1 | Supply, installation, testing and commissioning of chilled water type High static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3/G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping. The unit shall be suitable for 230 ± 10 volts, 50 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level.
B.1.1 | 2.0 TR - (800 CFM @ 50-70 PASCAL -ESP) | Nos | 1 |  | 0 |  | 0 | 0
B.1.2 | 5.0 TR - (2000 CFM @ 90-100 PASCAL -ESP) | Nos | 1 |  | 0 |  | 0 | 0
VENTILATION FANS
B.2 | Supply, Installation, Testing & commissioning of 25mm thick mineral wool insulated Double Skin Inline fresh air fans (With Pre-Fiter). Outer skin shall be 0.6 mm pre plasticized or powder coated GSS sheet. Inner sheet shall be 0.6 mm plain GSS perforated. Extruded Aluminum corners. Complete with Glass view panel, motor guard, marine light, limit switch, cable entry, GSS base frame. Screw less construction with zero leakage in the panel joints. Inspection door for all the sections. Fan: PLUG TYPE , IE - 3, Motor shall be suitable for Variable Frequency Drive along with control panel and necessary cabling. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Terminal box of the unit shall be IP54 rated. Quote shall be inclusive of all necessary mounting and fixing arrangements for the fan. Note : External Static Pressure (ESP) is calculated based on design drawing how ever contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.2.1 | 2400 CFM @ 250 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
B.2.2 | 4525 CFM @ 250 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
B.3 | Supply, Installation, Testing & Commissioning of Kitchen exhaust air Vane/Tube Axial flow type fans of approved make complete with aluminum alloy blades with aerofoil design, bird screen, flexible connection & gravity louvers at outlet. Motor shall be of IE 3, Motor shall be suitable for Variable Frequency Drive along with control panel and necessary cabling, the motor should be located outside of the hot air stream, Class H insulation. The unit shall be suitable for 400 ± 15 volts, 50 Hz, 3 phase AC supply. Sound level at 3 mtr distance from fan outlet shall not be more than 80 db(A).Including control panel and all necessary cabling and terminations. Fans should be AMCA certified for Air & Sound. Manufacturer shall submit “Certificate of conformity for 250 deg for 2 hours operation as per EN12101-3: 2002 issued by Internationally recognized Independent Fire Laboratory should be submitted along with type test report. The Type test report should clearly indicate the make of motor used during the testing and the same make/model of motor should be supplied by the fan manufacture at the site. RPM Should Not exceed 1450. However lower cfm up to 5000 CFM can be provided at 2850 RPM. Outlet velocity should not exceed 16 m/s. Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. Note : External Static Pressure (ESP) is calculated based on design drawing how ever contractor to select fan to match with actual pressure drop based on site condition. Pressure drop calculation and selection to be submitted to consultant for review / approval. The procurement shall be processed only after pressure drop calculations & selections duly verified from the consultants.
B.3.1 | 3000 CFM @ 600 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
B.3.2 | 5700 CFM @ 600 PASCAL - ESP. | Nos | 1 |  | 0 |  | 0 | 0
AIR CLEANING EQUIPMENTS
B.4 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Dry scrubber of approved make with minimum 25 mm thick mineral whool panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate . The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above.
B.4.1 | 3000 CFM | Nos | 1 |  | 0 |  | 0 | 0
B.4.2 | 5700 CFM | Nos | 1 |  | 0 |  | 0 | 0
C | AC PIPING AND ACCESSORIES
AC CONDENSATE DRAIN PIPE
C.1 | Supply, installation and testing of Rigid uPVC condensate drain water piping of approved make with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape.
C.1.1 | 25 mm Ø | Mtr | 8 |  | 0 |  | 0 | 0
AC CHILLED WATER PIPING
C.2 | Supply, installation and testing of MS class (C) Chilled water pipes with insulation of approved make with vapor barrier and finished with protective coating (Pidilite/Equivalent) over a layer of 7 Mil glass cloth for mechanical protection complete with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports etc. Piping insulation shall be expanded polyurethane foam with 36 kg/m3 minimum density, thickness as specified below, 85% minimum closed cell content and thermal conductivity of 0.019 W/m.k at 10°C. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works.
C.2.1 | 25 mm Ø - (Insulation - 30 mm thick) | Nos | 8 |  | 0 |  | 0 | 0
C.2.2 | 32 mm Ø - (Insulation - 30 mm thick) | Nos | 6 |  | 0 |  | 0 | 0
D | AC PIPING VALVES & ACCESSORIES
D.1 | Supply, installation, testing & Commissioning of FCU Valve Kit of approved make for HVAC fan coil units in heating/cooling systems for FCUs. Complete with pressure independent control valve with proportional linear actuator (Modulating type), three-way shut-off valves, integrated by-pass, Venturi device with pressure test ports , Shut Off valve with Strainer and pre-formed shell insulation made of PPE. Flexible connector with threaded nuts/clamps to be provided between the unit and kit of suitable length.
D.1.1 | 25 mm Ø | Nos | 1 |  | 0 |  | 0 | 0
D.1.2 | 32 mm Ø | Nos | 1 |  | 0 |  | 0 | 0
D.2 | Supply, Installation, Testing, and Commissioning Forged Brass Ball Valve of approved make with full bore lever operated with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled/hot water pipe insulation with threaded connection ends with all necessary fixing arrangements.
D.2.1 | 25 mm Ø | Nos | 2 |  | 0 |  | 0 | 0
D.2.2 | 32 mm Ø | Nos | 2 |  | 0 |  | 0 | 0
D.3 | Supply, Installation, Testing, and Commissioning BTU Meter of approved make with direct pipe connection type or operated via sensor module connected supply and return pipe with all necessary fixing and valve arrangements. LCD display (shows all water parameters), with flow rate, temperature inputs, data storage up to 365 days. The display panel shall be mounted at readable height and it shall include interconnecting wiring between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box with all necessary fixing arrangements. Unit shall be compatible with facility Building Management System. (Make and model shall be as per Airport requirement)
D.3.1 | 25 mm Ø | Nos | 1 |  | 0 |  | 0 | 0
D.3.2 | 32 mm Ø | Nos | 1 |  | 0 |  | 0 | 0
D.4 | Supply, Installation, Testing, and Commissioning of Forged Brass Drain Valve / Drain Cock, of approved make rubber seal, O rings e with all necessary fixing arrangements.
D.4.1 | Drain Valve connected in chilled water supply & return line | Nos | 4 |  | 0 |  | 0 | 0
D.5 | Supply, Installation, Testing, and Commissioning of Forged Brass Automatic Air Vent of approved make with all necessary fixing arrangements.
D.5.1 | Automatic Air Vent connected in chilled water supply & return line | Nos | 4 |  | 0 |  | 0 | 0
D.6 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements.
D.6.1 | Dial Size - 63 mm Ø | Nos | 4 |  | 0 |  | 0 | 0
D.7 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements.
D.7.1 | Dial Size - 63 mm Ø | Nos | 4 |  | 0 |  | 0 | 0
D.8 | Supply, installation, testing & commissioning of Test point of approved make with all necessary fixing arrangements..
D.8.1 | Test point for supply and return lines | Nos | 4 |  | 0 |  | 0 | 0
E | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
E.1 | Supply, installation and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) 120GSM Zinc coated factory fabricated Square / Rectangular Ducts of approved make with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
E.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.mtr | 23 |  | 0 |  | 0 | 0
E.1.2 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.mtr | 48 |  | 0 |  | 0 | 0
E.2 | Supply, installation, and testing of Black Steel (BS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectangular Ducts of approved make with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings, gaskets, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bolts, nuts, bolts, structural beam clamps as applicable. Duct and all other accessories shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
E.2.1 | 18 Gauge - (1.21 mm Thick) - Kitchen Exhaust Air Duct | Sq.mtr | 61 |  | 0 |  | 0 | 0
FLEXIBLE DUCTS
E.3 | Supply, installation, and testing of Insulated Flexible Duct Connectors (Canvas connection) of approved make to isolate vibrations and noises caused by air handling units or any other equipment's connected to the duct with air tight fittings with all necessary accessories.
E.3.1 | For FCU | Nos | 2 |  | 0 |  | 0 | 0
F | AIR DISTRIBUTION DUCT - THERMAL INSULATIONS & ACCOUSTIC LINNINGS
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
F.1 | Supply, installation of Thermal Insulation of approved make for duct insulation using closed-cell elastomeric nitrile rubber Class O rated as per BS 476 Part 6: 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg/m.s.Pa i.e. μ>7000: Water Vapor diffusion resistance) as per DIN 53122 part 2, DIN 52615 / EN 12086 & EN13469. Black Colour with having a density of 50 ± 10 Kg/M3. Quote shall be inclusive of necessary Adhesive.
F.1.2 | 13 mm thicknesses - (SAD) | Sq.mtr | 23 |  | 0 |  | 0 | 0
F.1.2 | 25 mm thicknesses - (FAD) | Sq.mtr | 48 |  | 0 |  | 0 | 0
F.2 | Supply, installation of Thermal Insulation of approved make for Kitchen exhaust ducting using rockwool with silver foil covering, density of 50 Kg/m3.Quoute shall be inclusive of necessary Adhesive.
F.2.1 | 25 mm thicknesses - (KEAD) - For Kitchen Exhaust | Sq.mtr | 61 |  | 0 |  | 0 | 0
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
F.3 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg/m3 Quote shall be inclusive of necessary Adhesive. Thermal conductivity of the insulation material shall not exceed 0.047 W/m K at an average temperature of 20°C.
F.3.1 | 15 mm thicknesses - (SAD) | Sq.mtr | 9 |  | 0 |  | 0 | 0
G | AIR DISTRIBUTION DUCT - DAMPERS
DUCT AIR CONTROL DAMPERS
G.1 | Supply, installation, testing and commissioning of aluminum powder coated Opposed Blade Damper / Collar Damper of approved make.
G.1.1 | Size - 600 x 150 mm | Nos | 2 |  | 0 |  | 0 | 0
G.1.2 | Size - 800 x 150 mm | Nos | 4 |  | 0 |  | 0 | 0
G.2 | Supply, installation, testing and commissioning of Aluminium powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.
G.2.1 | Size - 300 x 200 mm | Nos | 3 |  | 0 |  | 0 | 0
G.2.2 | Size - 350 x 250 mm | Nos | 6 |  | 0 |  | 0 | 0
G.2.3 | Size - 400 x 250 mm | Nos | 1 |  | 0 |  | 0 | 0
G.2.4 | Size - 500 x 350 mm | Nos | 1 |  | 0 |  | 0 | 0
G.2.5 | Size - 500 x 600 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3 | Supply, installation, testing and commissioning of MS powder coated Low Leakage Square / Rectangular Volume Control Damper of approved make with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt.(For Kitchen Exhaust MS duct)
G.3.1 | Size - 300 x 300 mm | Nos | 3 |  | 0 |  | 0 | 0
G.3.2 | Size - 350 x 350 mm | Nos | 6 |  | 0 |  | 0 | 0
G.3.3 | Size - 400 x 200 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3.4 | Size - 400 x 400 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3.5 | Size - 500 x 450 mm | Nos | 1 |  | 0 |  | 0 | 0
G.3.6 | Size - 500 x 600 mm | Nos | 1 |  | 0 |  | 0 | 0
H | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
H.1 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange with all necessary fixing arrangements. powder coated finish with RAL Colour as required by ID Designer / Architect.
H.1.1 | Neck Size - 150 mm X 600 - (2 - Way) | Nos | 4 |  | 0 |  | 0 | 0
H.1.2 | Neck Size - 150 mm X 800 - (2 - Way) | Nos | 2 |  | 0 |  | 0 | 0
H.1.3 | Neck Size - 150 mm X 800 - (1 - Way) | Nos | 2 |  | 0 |  | 0 | 0
H.2 | Supply, installation, testing and commissioning of Extruded Aluminium Linear Bar / Square Grille of approved make with fixed Aerofoil blades 15° deflection with frame of 20mm flange frame with 8 mm step suitable to tegular / grid type false ceiling with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.2.1 | Neck Size - 400 mm X 400 mm - (2 - Way) | Nos | 1 |  | 0 |  | 0 | 0
LOUVERS
H.3 | Supply, installation, and testing of Extruded Aluminium Fresh Air Sand Trap Louver of approved make with Bird screen and Wire mesh with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.3.1 | Size - 500 mm X 650 mm | Nos | 1 |  | 0 |  | 0 | 0
H.3.2 | Size - 950 mm X 650 mm | Nos | 1 |  | 0 |  | 0 | 0
H.4 | Supply, installation, testing and commissioning of Extruded Aluminium Exhaust Air Louver of approved make with 45 degree blades to avoid rain water penetrations continued with wire mesh and bird screen, 30 mm flange with all necessary fixing arrangements. Powder coated finish with RAL Colour as required by ID Designer / Architect.
H.4.1 | Size - 500 mm X 650 mm | Nos | 1 |  | 0 |  | 0 | 0
H.4.2 | Size - 1200 mm X 650 mm | Nos | 1 |  | 0 |  | 0 | 0
J | HVAC SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
J.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
J.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1 |  | 0 |  | 0 | 0
K | TESTING AND BALANCING
K.1 | Air balancing of Supply, Return, Fresh air and Exhaust air system to arrive as per design air flow rates |  |  | Lumpsum
K.2 | Water balancing of Entire Chilled and Hot Water piping system to arrive the designed flow rates. |  |  | Lumpsum
K.3 | Chilled water and Hot water pipe Pressure testing at 15kgf/cm2 hydrostatics pressure for a minimum 24hrs hold time .Testing should be done in the presence of Airport Concerned Persons. |  |  | Lumpsum
L | SHOP DRAWINGS & APPROVALS
L.1 | Preparation and submission of a detailed shop drawing for the HVAC system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like Electrical, Plumbing, and fire services, with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
M | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
M.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
M.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
M.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
M.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.