## GAS
BILL OF QUANTITIES
PROJECT: | IN-DXN-BRAJ KI GALIYAN (FOOD MAHAL) | [5 empty] | DATE: | 2024-12-09
[7 empty] | REV: | R0
GAS SERVICES - BILL OF QUANTITIES | [6 empty] | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at the site and also with Airport authorities whether there are provisions at the site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions, etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM | DESCRIPTION | UNITS | QTY | MATERIAL COST |  | LABOUR COST |  | TOTAL AMOUNT
|  |  |  | UNIT COST | TOTAL | UNIT COST | TOTAL
|  |  |  | (INR) | (INR) | (INR) | (INR) | (INR)
A | CONNECTING / INTEGRATING UNIT MandE SERVICES TO AIRPORT MandE SERVICES/ BUILDING
A.1 | If any termination or connection of the unit services is required outside the site location (i.e., connection/termination of the MEP unit to the airport MEP service or airport external façade or roof, etc.), then the contractor has to work in consultation with the airport to plan, design, and detail such connections. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Finally, the contractor is to make good on any penetrations after installation, including providing fire seals as required as per airport requirements. |  |  | Provisional Sum
B | GAS SYSTEMS
GAS SUPPLY EQUIPMENTS & METERING
B.1 | Supply, Installation, Testing, and Commissioning of Gas Meter with a maximum pressure range of 0.5 Bar or as per Airport guidelines or standards, operating temperature range of -20°C to +60°C, of approved make and with all necessary fittings and connectors, etc.
B.1.1 | Max flow rate - 10 m3/h | Nos | 1 |  | 0 |  | 0 | 0
GAS SUPPLY PIPE VALVES & ACCESSORIES
B.2 | Supply, Installation, Testing, and Commissioning of Chrome Plated Brass Ball Valve with double O-ring stem, nut with anti-corrosion coating, and steel lever handle with anti-corrosion treatment and PVC coating, suitable for Gas pipe service of approved make and with all necessary fittings and connectors, etc.
B.2.1 | 32 mm Dia | Nos | 3 |  | 0 |  | 0 | 0
B.3 | Supply, Installation, Testing, and Commissioning of Gas Solenoid Valve with manual reset, operating pressure 6 Bar, operating temperature range -15°C to +60°C with a protection class of IP65 of approved make with integration to Gas leak detection, Kitchen Fire suppression systems, and Fire alarm systems as per Airport guidelines or standards requirement and with all necessary fitting and connectors, etc.
B.3.1 | 20 mm Dia | Nos | 2 |  | 0 |  | 0 | 0
B.4 | Supply, Installation, Testing, and Commissioning of Automatic Gas Shutt-off Valve of approved make and with all necessary fitting and connectors
B.4.1 | 25 mm Dia | Nos | 1 |  | 0 |  | 0 | 0
B.5 | Supply, Installation, Testing, and Commissioning of Second Stage Regulator with adjustable pressure control, inlet pressure of 0.5 Bar, and outlet pressure to suit the kitchen equipment of approved make and with all necessary fittings and connectors, etc.
B.5.1 | 40 kg/h - Flow Rate | Nos | 5 |  | 0 |  | 0 | 0
B.6 | Supply, Installation, Testing, and Commissioning of Pressure Guage with a range of 0 - 30 PSI (0 - 2 Bar) and 63 mm dial size of approved make and with all necessary fittings, isolation valves and connectors, etc.
B.6.1 | 1/4 - inch NPT on bottom Connection | Nos | 2 |  | 0 |  | 0 | 0
GAS SUPPLY PIPING
B.7 | Supply, Installation, Testing, and commissioning of Schedule 40 Carbon Steel Pipe with all necessary fittings such as bends, elbows, tees, reducers, unions, threading, cutting and welding etc. The pipes are to be applied with 2 coats of primer and 2 coats of enamel finish paint of approved color and with proper pipe supports necessary as per standards and site condition/requirements. Complete pipeline to be flushed with Nitrogen before commissioning of the system.
B.7.3 | 15 mm Dia | Mtr | 2 |  | 0 |  | 0 | 0
B.7.4 | 20 mm Dia | Mtr | 6 |  | 0 |  | 0 | 0
B.7.5 | 25 mm Dia | Mtr | 8 |  | 0 |  | 0 | 0
B.7.6 | 32 mm Dia | Mtr | 8 |  | 0 |  | 0 | 0
B.8 | Supply, Installation, Testing, and commissioning of Corrugated Stainless Steel Flexible Gas Pipe (CSST) conforming to BS EN 15266 with an operating pressure of 0.5 Bar, UV resistant PVC jacket, and all necessary fittings such as adapters, couplers, tees, nipples, reducers, nuts, washers, gasket, and necessary connections, etc. Proper pipe supports are necessary as per standards and site conditions/requirements.
B.8.1 | 15 mm Dia | Mtr | 5 |  | 0 |  | 0 | 0
C | GAS SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
C.1 | All services for pipes Like Type of Gas, pipe size, Flow direction need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
C.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1
D | TESTING & COMMISSIONING
D.1 | Pressure test for Gas supply piping system for leak detection
D.1.1 | Gas piping systems are to be tested at the site with a test pressure three times the working or operating pressure recommended as per airport design guidelines for a holding time period of at least 30 minutes. The test is to be conducted after the complete installation of all gas supply pipes, including all valves and accessories, as per the proposed design. | Set | 1 | Lumpsum
E | SHOP DRAWINGS & APPROVALS
E.1 | Preparation and submission of a detailed shop drawing for the gas piping system after a thorough study of design drawings, site surveys, and relevant airport standards with correct routing, size, and elevations. The drawings also need to be coordinated with other MEP services like HVAC, Electrical, Plumbing, and Fire along with the latest Architectural and Interior design drawings, before construction. Necessary amendments to the drawings are to be made and resubmitted in case of any variations on site while at the construction stage of the project. Also prepare relevant detailed connection drawings as per selected manufacturer details and Airport standards, with necessary approval to be obtained from consultants and authority/regulatory bodies having jurisdiction, along with material submission approval with airport authorities. |  |  | Lumpsum
F | MISCELLANEOUS OR ANY ADDITIONAL ITEMS
F.1 | The contractor needs to mention any additional items or missing items that are not mentioned in the above BOQ after a detailed site survey or inspection and to be validated by consultants.
F.1.1 | Item 1 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
F.1.2 | Item 2 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
F.1.3 | Item 3 - (Contractor to describe only if there are any) | Unit | 1 |  | 0 |  | 0 | 0
GRAND TOTAL
Note : This BOQ is issued for costing purposes only; necessary corrections or amendments are to be made based on selected items, manufacturer details, site conditions, airports, and local regulatory or approval bodies having jurisdictional requirements and necessary approvals to be made for equipment's and material submission prior to procurement. The quantities mentioned in the above BOQ include services only inside the site location (building). If any termination of services is required outside the site location, the contractor must verify at the site and provide the quantity and cost over and above this BOQ.