## F-F-042_ELEC BOQ
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | FF42_BRIOCHE DOREE_HYDERABAD AIRPORT |  |  | DATE: | 2024-02-07
|  |  |  | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
Item Code | Item Name | UOM | Qty | UNIT COST | REMARKS
A | METER / METER PANEL
A.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). Energy Meter shall be of Digital kVAH Type and Make / Manufacturer from below list, or any other make with kVAH option with Approval from TS Department. For Make refer list below, Single Phase (For load below 40A) : Make - MID (Algodue Electronica), Model - UEM 40-2C. Type - Direct. Three Phase (For load below 60A) : Make - Secure, Model - Sprint 350, Type - Direct. Three Phase (For load above 60A) : 1) Make - Secure, Model - Elite 445, Type - C.T. 2) Make - Conzerv (Schneider Electric), Model - EM6438, Type - C.T. 3) Make - L & T, Model - Vega TM (WDM303FDWA1), Type - C.T.
A.1.1 | 80/5A ENERGY METER (CT TYPE) | No. | 1
B | LV CABLING
B.1 | Supply, Installation, Testing & Commissioning of Fire Rated LS/LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Brass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench as required. Make : Electrical Wires & Cables : Finolex, Polycab, RR Kables, KEI or equivalent. For cables laid on Cable Tray / in Pipe / on Wall / Trench - the rate shall include necessary supporting / clamping arrangements.
B.1.1 | 4C x 35 MM2 | Mtr. | 10
B.1.2 | 4C x 25 MM2 | Mtr. | 10
C | DISTRIBUTION BOARDS
C.1 | Supply, Installation, Testing & Commissioning of Surface / Flush mounting 10kA / 25kA (As per Panel requirement) Distribution Boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including inter connecting wiring & earth bus on insulation mount. Make : Electrical Panel / DB's & Breakers (MCB, RCBO, ELCB & MCCB) : Legrand, Siemens, ABB, Schneider or equivalent. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall be Hpi / Si series & MCB's shall be 'B" / 'C' Curve (As per requirement).
LPDB
C.1.2 | 10 Way TPN Panel Board with 80A 4P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. | No. | 1
UPS DB
C.1.3 | 4 Way SPN Panel Board with 20A 2P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. | No. | 1
D | LIGHT FIXTURES POINT WIRING
D.1 | Supply, Installation, Testing & Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with Lamps, Ballasts / Drivers / Starters, Switches / Lighting Control Switch Board with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Light Fixtures : Philips, Wipro, Crompton, Syska or equivalent. Make : PVC Conduits : Sudhakar, Shakti or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
D.1.1 | WALL MOUNT GLOBE LIGHT (Point Wiring only) | Nos. | 13
D.1.2 | PANEL LIGHT (Point Wiring only) | Nos. | 10
D.1.3 | LED STRIP LIGHT WITH DIFFUSER (Point Wiring only) (50 mtr) | Nos. | 1
D.1.4 | SIGNAGE LIGHTS | Nos. | 2
D.1.5 | Lighting Control Switch board with switches as required (Point Wiring only) | Nos. | 1
E | WIRING DEVICES (SWITCHES & SOCKETS)
E.1 | Supply, Installation, Testing & Commissioning of Wiring Devices (Switches & Sockets - Face Plate Finish as approved by Architect / Matching to Architecture Finishes) with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Switch & Sockets : Anchor Roma / Penta, Legrand, Havells Crabtree, Finolex, L & T Switchgear or equivalent. Make : PVC Conduits : Sudhakar, Shakti or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
E.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 12
E.1.2 | 13A DUAL SWITCHED SOCKET OUTLET | Nos. | 4
E.1.3 | 13A SINGLE SWITCHED SOCKET OUTLET + USB PORT | Nos. | 8
E.1.4 | 13A DUAL SWITCHED SOCKET OUTLET + USB PORT | Nos. | 2
E.1.5 | 16A SINGLE SWITCHED SOCKET OUTLET | Nos. | 10
E.1.6 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 1
E.1.7 | 16A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET | Nos. | 5
E.1.8 | 20A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET | Nos. | 2
E.1.9 | 32A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET | Nos. | 1
E.1.10 | 32A THREE PHASE INDUSTRAIL SWITCHED SOCKET | Nos. | 1
F | CONTAINMENT (CABLE TRAY & TRUNKING)
F.1 | Supply & Installation of GI Cable Tray & GI Cable Trunking, through Wall / Ceiling / Floor as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc. Make : Cable Management System : Dudhat, Super, K.R. Power supports or equivalent with Airport approval.
F.1.1 | 50 x 50 MM CABLE TRUNKING | Mtr. | 12
G | UPS SYSTEM
G.1 | Supply, Installation, Testing & Commissioning of UPS along with required Battery for specified back-up time, complete with Battery Stand (If required) & standard accessories / equipments required for complete functioning of the system, earthing, support system (if required), etc. Make : UPS System : Luminous, APC, Microtek or equivalent with Airport approval.
G.1.1 | 1.5KVA Single phase UPS with 30 Minute Back-up | Nos. | 1
H | CCTV SYSTEM
H.1 | Supply, Installation, Testing & Commissioning of CCTV System with suitable / required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console / DVR, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : CCTV System : Hikvision, Honeywell, Dahua, or equivalent with Airport approval. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
H.1.1 | CCTV Dome Camera, 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. | Nos. | 4
H.1.2 | CCTV IP Dome Camera (CAT 6), 4 Megapixel / As approved or confirmed by client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. | Nos. | 1
H.1.3 | DVR with 45 Days Back-up | Nos. | 1
I | DATA NETWORK SYSTEM
I.1 | Supply, Installation, Testing & Commissioning of Data & Telephone Network System with required cabling through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : IT Cables & Accessories : Belden (Part Code - 7834ANC). The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
I.1.1 | Single Data outlet (RJ45) Jack | Nos. | 4
I.1.2 | Dual Data outlet (RJ45) Jack | Nos. | 2
I.1.3 | Patch Cords (1.5 meters length) | Nos. | 8
GRAND TOTAL NET
NOTE : The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.