## Elec_Inventory
INVENTORY FOR ELECTRICAL WORKS
KFC-DSHA-FF 041-AIRPORT,HYDERABAD
SR. NO. | DESCRIPTION | QTY | UNIT | Basic Rate | Amount
1 | Supply items
a | Supply of Main LT panels | 1 | Nos |  | 0
b | Supply of 14 Way TPNDB | 0 | Nos |  | 0
c | Supply of 18 Way SPNDB | 0 | Nos |  | 0
d | Supply of 16 Way SPNDB | 1 | Nos |  | 0
e | Supply of 12 Way TPNDB | 1 | Nos |  | 0
f | Supply of 8 Way VTPNDB | 0 | Nos |  | 0
2 | UPS
2.01 | Supply,Installation,Testing & Commissioing of single/Three phase UPS with 20minute battery back-up online systems with 2 nos DP MCB in weather proof enclosures. 3KVA -single phase input and single phase output ups with 25A DP MCB and 25A DP MCB on input and output of ups. 6KVA - single phase input and single phase output ups with 40A DP MCB and 40A DP MCB on input and output of ups.
a | 3 KVA Rack Mounted | 0 | Nos | 0 | 0
b | 6 KVA Rack Mounted | 0 | Nos | 0 | 0
c | 3 KVA Floor Mounted | 1 | Nos | 0 | 0
d | 6 KVA Floor Mounted | 1 | Nos | 0 | 0
3 | STABILIZER |  |  |  |  | AIRPORT SCOPE
3.01 | Supply,Installation,Testing & Commissioing of 3 PHASE, INUPT VOLTAGE : 350-480V, OUTPUT VOLTAGE ACCURACY : ± 1%, LINE FREQUENCY VARIATION: 47Hz - 53Hz, RESPONSE TIME : 10ms, PROTECTION: Automatic switch off against -Undervoltage/Overvoltage, Overload/Underload, Single Phasing, SURGE PROTECTION : Class C Type Secondary Surge Protection.
a | 75 KVA | 0 | Nos | 0 | 0
b | 100 KVA | 0 | Nos | 0 | 0
c | 125 KVA | 0 | Nos | 0 | 0
d | 150 KVA | 0 | Nos | 0 | 0
4 | DIESEL GENERATOR SET |  |  |  |  | AIRPORT SCOPE
4.01 | Supply,Installation,Testing & Commissioing of Automatic type diesel generator with canopy,base MS frame,fuel tank & all necessary acessories. DG set should contain all required spare & parts. DG should be 3 phase 440V/3PH/50Hz.The diesel engines shall be of the direct injection, four stroke , Inline, with Radiator cooled , turbo charged with charged air cooled operating at a nominal speed of 1500 RPM. The engine fitments shall include but not be limited to the following:- i) Flexible coupling/Close Coupled alternator and flywheel. ii) Dry type air filter with clogged condition indicator (The filter shall be easily approachable for maintenance). iii) Radiator inbuilt in the common skid base frame and Engine suitable to run the DG set at 10% overload at an ambient of 50 Degrees centigrade, keeping the acoustic doors in closed condition. iv) Engine driven fuel pump. v) Engine driven coolant pump. vi) Engine driven lubricant Lube oil pump, oil cooler and filter. vii) Silencers with Hospital Grade only viii) 12V D.C. Starter & battery charging alternator. ix) Microprocessor based monitoring & control system capable of operator interface to the DG set manually and remote start/stop control and shut down fault indication shall be of electronic LCD type displaying Engine and Alternator parameters. x) AMF cum auto changover panel should be considered with DG
a | 62.5 KVA | 0 | Nos | 0 | 0
b | 82.5 KVA | 0 | Nos | 0 | 0
c | 100 KVA | 0 | Nos | 0 | 0
d | 125 KVA | 0 | Nos | 0 | 0
| Amount | 5 |  |  | 0
| GST 18% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0