## SKY HIGH BIRYANI
R0
|  |  |  | DATE | 13.12.2024
SKY HIGH BIRYANI @DELHI T3
BOQ FOR FIRE FIGHTING SYSTEMS
S/NO | DESCRIPTION | QUANTITY | UNIT | Rate | Amount
1 | Providing , fixing testing and commissioning of pendant type sprinkler heads 68 deg. Temp | 7 | No.
2 | Providing , fixing testing and commissioning of pendant type sprinkler heads 79 deg. Temp | 3 | No.
3 | Providing , fixing testing and commissioning of upright type sprinkler heads 68 deg. Temp | R.O. | No.
4 | Providing , fixing testing and commissioning of upright type sprinkler heads 79 deg. Temp | R.O. | No.
5 | Providing , fixing testing and commissioning of recessed ( concealed ) type sprinkler heads | R.O. | No.
6 | Providing & fixing testing and commissioning of UL Rated SS Flexible pipe ( Assumed required at site)
a | 1000 MM Long | 7 | No.
b | 1200 MM Long |  | No.
c | 1600 MM Long | 3 | No.
d | Providing & fixing testing and commissioning of UL/FM approved Rated crome finished rosset cap TYCO/VIKING MAKE | 10 | No.
7 | Providing, laying, jointing, testing and commissioning of G.I. pipes and fittings (IS:1239 (Part-I)-Class "C" and IS:1239 Part-II heavey respectively), All pipes as per ASTM A-105/3000 LBS (up to 50mm dia) and ASTM A:234 WPB or B above 50mm dia including cutting,threading welding etc providing all malleable galvanized iron fittings viz. Flanges, bends, tees, elbows,reducers, unions, supporting with G. I. clamps, hangers, M.S. brackets etc. including cutting holes and chases in brick or RCC wall / slabs and making good the same to the Approval of Architect / consultant,complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade. (Pipe connection shall be thredded up to 50mm dia and above 50mm dia shalll be through welding)
I) | 25 mm dia. | 18 | RMT
ii) | 32 mm dia. | 5 | RMT
Iii) | 40 mm dia. | 2 | RMT
iv) | 50 mm dia. | 10 | RMT
v) | 65 mm dia. | 0 | RMT
vi) | 80 mm dia. | 0 | RMT
8 | Wheel operated Butterfly Valves (PN 16) with inbuilt supervisory switch (UL listed and FM approved) with CI Body, Black Nitrile Body Liner and Nylon Coated SG Iron Disc with material and labour including hydraulic testing etc. complete as per drawing, specification & to the level of satisfaction of Site- Incharge.
I) | 65 mm dia. | 0 | No.
iI) | 50 mm dia. | 1 | No.
SUB-TOTAL
GRAND TOTAL
General
Notes :
1) Taxes Extra as applicable.
2) Contractor to read the drawings with BOQ and quote accordigly, Deviation if any shall be confirmed by contcator prior to finalise the order.
General Guidelines (FPS).
AFC/Upright Sprinklers are subjected to void space and obstruction/double layer ceiling, to be done by concessionaire.
Entire area to be covered under sprinkler coverage area without any blind spots.
Sprinkler should be installed in accordance with NFPA-13 and Shared Airport guidelines .
Pipes and fittings shall be confirming to IS 1239 Part -1 Class “C” Heavy
Tyco- 68 degree concealed & Pendent type , It shall be QR (Quick Response), Discharge Coefficient K=5.6 with Cover plates of same make, both shall be UL Listed & FM Approved. Make-Tyco, Viking.
For cooking area and Hood suppression area- 79 degree Concealed & Pendant type, It shall be QR (Quick Response), Discharge Coefficient K=5.6 with Cover plates of same make, both shall be UL Listed & FM Approved
All areas need to be covered with Sprinkler System. All dimensions need to be mentioned in drawing. “Sprinkler to Sprinkler” & “Sprinkler to Partition/Obstruction/bulkhead/etc.” distance should not be more than 3000MM & 1500MM respectively.
Testing should be done @15kgf/Cm hydrostatics pressure for 24 hrs hold time post installation IR cleared by DAIL-Engg. Testing should be witnessed to DAIL-Engg
600mmx600mm access trap door should be provided in false ceiling at each and every location of MEP tap off /isolation valve/VCD. Trap door should be provided at each and every cabin /room/partition area/obstructed area ceiling void for O&M of MEP services installed above ceiling area .
Hose pipe- Tyco-1500 mm long UL listed FM approved, It shall be 1500MM S.S. Braided, UL Listed & FM Approved.
Minimum distance between two wielded joints should not be less than 100mm. Bushes are not allowed only concentric reducers are allowed to reduce pipe sizes.
Downwards tapping of branches from header is not allowed, only side and top tapping should be done w.r.t branch piping. Flexible should be connected to branch horizontal for making proper circulation bending while fixing at false ceiling level upward and downward used connection of flexible to branches are not allowed. 'Sprinkler to sprinkler' & 'sprinkler to partition\ bulkhead\obstruction' distance should not be less than 3000mm & 1500mm respectively. And for side wall sprinkler spacing shall be as per specified (type) details. A sprinkler should be installed in such a way that these should be no hindrance in spray pattern and coverage area of any sprinkler due to any other services / installation / texture/ change in false ceiling level/ etc.
Sprinkler Installation may need be adjusted/changed as per NFPA guidelines, if any obstructions in coverage area due to ceiling elevations/design
If any changes in other drawings (MEP ,Civil & Interior) sprinkler drawing to be revised accordingly and prior information to be shared to DIAL
Note: Sprinklers and Detectors Installation may need be adjusted/changed as per NFPA guidelines, if any obstructions in coverage area due to ceiling elevations/design.