## SUMMARY
NON ALCOHOLIC - AHMEDABAD AIRPORT
SUMMARY FOR ELECTRICAL LOAD
REVISION: R0, DATE: 13.01.2024
Sr.No. | DESCRIPTION | WATTAGE (KW) | No of Units | CONNECTED LOAD | MAX. DMD LOAD | DIVERSITY | UPS LOAD
1 | LIGHTING LOAD
a | 600x600mm PANEL LIGHT | 30 | 6 | 0.18 | 0.162 | 90%
b | SURFACE LIGHT | 22 | 36 | 0.792 | 0.7128 | 90% | 0.792
c | PENDANT LIGHT-1 | 18 | 4 | 0.072 | 0.0648 | 90%
d | PENDANT LIGHT-2 | 18 | 0 | 0 | 0 | 90%
e | HANGING LIGHT | 12 | 20 | 0.24 | 0.216 | 90%
f | DECORATIVE WALL LIGHT | 12 | 5 | 0.06 | 0.054 | 90%
g | LED STRIP LIGHT | 22 | 5 | 0.11 | 0.099 | 90%
h | HOOD LIGHT | 10 | 2 | 0.02 | 0.018 | 90%
i | 600x600mm PANEL LIGHT (Emg) | 30 | 2 | 0.06 | 0.054 | 90% | 0.06
j | PENDANT LIGHT-1 (Emg) | 18 | 0 | 0 | 0 | 90% | 0
2 | RAW POWER LOAD
| 6/16A Utlity sockets | 0.1 | 35 | 3.5 | 1.4 | 40%
| USB | 0.01 | 40 | 0.4 | 0.16 | 40%
| POS counters | 0.3 | 2 | 0.6 | 0.48 | 80% | 0.6
| KOT | 0.2 | 0 | 0 | 0 | 100% | 0
| Chilling Machine | 1 | 0 | 0 | 0 | 100% | 0
| Self Service Kiosk | 0.25 | 0 | 0 | 0 | 100%
| Signage | 0.5 | 5 | 2.5 | 2.5 | 100% | 2.5
| R.O. Plant | 0.15 | 0 | 0 | 0 | 100%
| Service Station | 0.3 | 0 | 0 | 0 | 100%
| TV | 0.25 | 1 | 0.25 | 0.25 | 100% | 0.25
| GAS SUPPRESSION SYETEM | 0.15 | 1 | 0.15 | 0.15 | 100% | 0.15
| FIRE SUPPRESSION SYSTEM | 0.15 | 1 | 0.15 | 0.15 | 100% | 0.15
3 | HVAC LOAD
| AHU | 2.2 | 1 | 2.2 | 1.76 | 80%
0
4 | KITCHEN EQUIPMENTS |  |  | 25.718 | 18.0026 | 70%
5 | FRESH AIR | 3.7 | 1 | 3.7 | 2.96 | 80%
6 | EXHAUST AIR | 3.7 | 1 | 3.7 | 2.96 | 80%
.
7 | MISCELLANEOUS |  |  | 1 | 0.5 | 50%
| TOTAL LOAD IN KW |  |  | 45.402 | 32.6532 |  | 4.502
UPS CALCULATIONS
| Total C & S Load | [5 empty] | 4502
| TOTAL EMERGENCY LOAD 15% of total lighting load | [5 empty] | 0.525
| TOTAL UPS LOAD | [5 empty] | 4502.525
| Load Factor 80% - UPS Load shall be (WATTAGE) | [5 empty] | 3602.02
| After considering 0.85 power factor - VA Rating | [5 empty] | 4237.6706
| Efficiency 80% - UPS Rating shall be (VA) | [5 empty] | 5297.0882
| Recommended UPS rating (KVA) -1PH. I/C & O/G .(with Plus Minus 5%) | [5 empty] | 5.2971
| Nearest size available--(1#5KVA) | [5 empty] | 5
.

## Kitchen BOQ
SR.NO. | DESCRIPTION | OVERALL SIZE | QTY | Make | Model | ELECTRICAL |  |  |  | PLUMBING | [5 empty] | LPG / PNG |  |  | EXHAUST CFM | Tap Brand | Tap Model Number | Tap Photo | REMARK
|  | All Dimensions in MM L x W x H |  |  |  | HP | Watts | ELECTRICAL LOAD IN KW | PHASE | HOT | COLD | RO | Line Pressure | WASTE | Type of Burner | NO OF BURNER | Consumption Per Burner Per Hour / KG | BTU Per Burner Per Hour
[24 empty] | R PHASE | Y PHASE | B PHASE
MK - 01 | Four Burner Range With One Under Shelve | 765 x 765 x 850 + 150 | 1 | CUSTOM FABRICATED | [10 empty] | G 10 | 4 | 1.58 | 70000
MK - 02 | Part Hot Plate / Part Griddle Plate | 600 x 765 x 850 + 150 | 1 | CUSTOM FABRICATED | [10 empty] | V | 2 | 1.58 | 70000
MK - 03 | Side Table With 2 U/S | 330 x 765 x 850 + 150 | 1 | CUSTOM FABRICATED
MK - 04 | Condiment Trolley | 375 x 575 x 700 | 1 | CUSTOM FABRICATED
MK - 05 | Two Burner Chinese Range | 900 x 850 x 800 + 350 | 1 | CUSTOM FABRICATED | [10 empty] | T 78 / G -8 | 2 | 3.56 /0.9 | 160000/40000
MK - 06 | Side Table With 2 U/S | 300 x 765 x 850 + 150 | 1 | CUSTOM FABRICATED
MK - 07 | Twin Basket Deep Fat Fryer ( Twin Basket 1/2 GN Pan Size ) | 625 x 765 x 850 + 150 | 1 | CUSTOM FABRICATED |  |  | 3000 x 2 | 6 | I | [14 empty] | 3 |  | 3
MK - 08 | Side Table With 2 U/S | 400 x 765 x 850 + 150 | 1 | CUSTOM FABRICATED
MK - 09 | Combi - Oven Table With Tray Arrangements
MK - 10 | Mini Combi Oven - To accommodate 5 Trays 2/3 Size | 535 x 672 x 649 | 1 | Unox | XECC-0523-E1RM |  |  | 5.5 | III |  |  | 19 | 29 Psi / 2 Bar | 100
MK - 11 | G.N. Size 2 Door Vertical Deep freezer | 700 x 818 x 1990 | 1 | HOSHIZAKI | HFW-77MS4-IC / LS4-IC | .75 HP | 0.56 | 0.56 | I | [14 empty] | 0.56
MK - 12 | G.N. Size 2 Door Vertical Chiller | 700 x 818 x 1990 | 1 | HOSHIZAKI | HRW-77MS4 / LS4 | .75 HP | 0.56 | 0.56 | I | [16 empty] | 0.56
MK - 13 | Spare Number
MK - 14 | Two Door Work Top Refrigerator with 1 Row of 1/6 G/N pans on top ( Compressor on LHS ) | 1200 x 700 x 850 | 1 | HOSHIZAKI | RTW-127MS4-GN /LS4-GN | .5 HP | 0.375 | 0.375 | I | [15 empty] | 0.375
MK - 15 | Two Door Work Top Refrigerator with 1 Row of 1/6 G/N pans on top ( Compressor on LHS ) | 1200 x 700 x 850 | 1 | HOSHIZAKI | RTW-127MS4-GN /LS4-GN | .5 HP | 0.375 | 0.375 | I | [14 empty] | 0.375
MK - 16 | Sink Unit - To be Provided with Mixer Tap | 400 x 840 x 838 + 150 | 1 | CUSTOM FABRICATED | [5 empty] | 12 | 12 |  |  | 100 | [5 empty] | JAQUAR | FLR-CHR-5167NB
MK - 17 | Grease Trap | 337 x 404 x 303 | 1 | Nugreen | NGT 14
MK - 18 | Wall Shelves | 850 x 300 | 2 | CUSTOM FABRICATED
MK - 19 | Work Table with Cross Bracing | 850 x 600 x 850 + 150 | 1 | CUSTOM FABRICATED
MK - 20 | Plate Counter With 2 U/S - Three Sides Covered | 1200 x 400 x 850 | 1 | CUSTOM FABRICATED
MK - 21 | Plate Counter With 2 U/S - Three Sides Covered | 1200 x 400 x 850 | 1 | CUSTOM FABRICATED
MK - 22 | Spare Number
MK - 23 | Ceiling Suspended OHS - Two Tier ( To be mounted at height of 450 MM from Counter Top) | 1200 x 300 x 450 + 300 | 1 | CUSTOM FABRICATED
MK - 24 | Ceiling Suspended OHS - Two Tier ( To be mounted at height of 450 MM from Counter Top) | 1200 x 300 x 450 + 300 | 1 | CUSTOM FABRICATED
DISHWASH AREA
DW - 01 | Hand Sink to be provided with Mixer Faucet | 350 x 390 x 216 + 100 MM SB (Three Sides) | 1 | Custom Fabricated | [5 empty] | 12 | 12 |  |  | 100 | [5 empty] | JAQUAR | FLR-CHR-5033B
DW - 02 | Slim Bin - Dry Waste Bin 60 Litres Capacity | 584 x 304 x 765 | 1 | Frontier | FLB SLIM | [12 empty] | FLB SLIM
DW - 03 | Soiled Dish Table With Sunk of 50 MM | 900 x 550 x 850 + 150 | 1 | Custom Fabricated | [9 empty] | 100
DW - 04 | Wet Garbage Bin - 80 Litres Capacity ( To provide with Dolly) | Dia 505 x 614 Height | 1 | Frontier | FLB80
DW - 05 | Grease Trap | 400 x 562 x 375 | 1 | Nugreen | NGT 40
DW - 06 | Pre Rinse Shower | IMPORTED | 1 | T&S | B-0123-B
DW - 07 | Under Counter Dish Washing Machine | 610 x 600 x 820 | 1 | Electrolux | 400153 |  |  | 5.35 | I |  | 12 |  | 100 | [11 empty] | 5.35
DW - 08 | Wall Shelves | 1250 x 300 | 2 | CUSTOM FABRICATED
DW - 09 | Pre - Rinse Table with Space for keeping Dish Wash Rack | 2200 x 700 x 850 + 150 | 1 | CUSTOM FABRICATED | [5 empty] | 12 | 12 |  | 100
DW - 10 | Side Table With Cross Bracing | 500 x 700 x 850 + 150 | 1 | CUSTOM FABRICATED
DW - 11 | Wall Shelves | 500 x 300 | 2 | CUSTOM FABRICATED
DW - 12 | Clean Dish Storage Rack - 5 Shelves ( 3 Sides Up and 1 Side Down ) | 500 x 500 x 1950 | 1 | CUSTOM FABRICATED
DW - 13 | Spare Number
DW - 14 | Pot / Pan Rack - 5 Shelves | 500 x 500 x 1950 | 1 | CUSTOM FABRICATED
Drain Grating
DG -01 | SS Drain Grating | 350 x 350 | 3 | CUSTOM FABRICATED
DG -01 | SS Drain Grating | 1450 x 200 | 1 | CUSTOM FABRICATED
Exhaust Hood
EX-01 | Exhaust Hood With SS Filters | 4775 x 1000 x 500 | 1 | CUSTOM FABRICATED | [14 empty] | 6200
OTHER ITEM
EXT1 | Water Boiler (Geyser) | 35 Lits. Capacity | 1 |  |  |  | 3000 | 3 | I | [16 empty] | 3
EXT2 | Air Curtain | BRANDED : 900mm Length | 1 | TECHNOCRAT | SLEEK | 1/2 HP | 0.375 | 0.375 | I | [14 empty] | 0.375
EXT3 | Insect Killer | BRANDED | 1 | TECHNOCRAT |  | 1/2 HP | 0.75 | 0.75 | I | [14 empty] | 0.75
EXT5 | Exhaust System |  | 1
EXT6 | Fresh - Air System |  | 1
| TOTAL | [22 empty] | 5.06 | 5.725 | 6.56
17.345

## BAR BOQ
SR.NO. | DESCRIPTION | OVERALL SIZE | QTY | Make | Model | ELECTRICAL |  |  |  | PLUMBING |  |  |  |  | LPG / PNG |  |  | EXHAUST CFM | Tape Model Number | Tape Photo | REMARK
|  | All Dimensions in MM L x W x H |  |  |  | HP | Watts | ELECTRICAL LOAD IN KW | PHASE | HOT | COLD | RO | WASTE | Type of Burner | NO OF BURNER | Consumption Per Burner Per Hour | BTU Per Burner Per Hour
[22 empty] | R PHASE | Y PHASE | B PHASE
BR - 01 | Blender Station | 600 x 600 x 800 + 50 | 1 | CUSTOM FABRICATED | [5 empty] | 12 |  | 12 | 100
BR - 02 | Blender | 213 x 200 x 416 | 1 | JTC | TM -800 | 0.6 |  | 0.6 | I | [12 empty] | 0.6
BR - 03 | Cocktail Station | 750 x 600 x 800 + 50 | 1 | CUSTOM FABRICATED | [8 empty] | 100
BR - 04 | Back Bar Bottle Cooler | 900 x 534 x 889 | 1 | ELANPRO | EBB2D | 1/2 HP | 0.373 | 0.373 | I | [12 empty] | 0.373
BR - 05 | POS |  | 1 | IT Scope
BR - 06 | Counter for POS (Size is Approx ) | 800 x 600 x 800 | 1 | Interior Designer Scope
BR - 07 | Counter With Space for Co2 Cylinders and Dust Bin | 640 x 600 x 950 | 1 | Interior Designer Scope
BR - 08 | Slim Bin - Dry Waste Bin 60 Litres Capacity | 584 x 304 x 765 | 1 | Frontier | FLB SLIM
BR - 09 | Coke Machine |  | 1 | Coke Company | [7 empty] | 12
BR - 10 | Tea Vending Machine |  | 1
BR - 11 | Ice Cube Machine | 534 x 534 x 685 | 1 | Celfrost | IC - 50 |  |  |  | I |  |  | 12 | 100
BR - 12 | Single Pod Coffee Machine | 406 x 535 x 559 | 1 | Lavazza | Nouvasimonrlli - Appia |  |  | 3.6 | I |  |  | 12 | 100 | [10 empty] | 3.6
BR - 13 | Spare Number
BR - 14 | Knock Box | 120 x 100 x 125 | 1 | Amazon | Akway
BR - 15 | Coffee Grinder | 220 x 360 x 430 | 1 | LaCimbali | Junior Manual Grinder |  | 300 Watts | 0.3 | I | [12 empty] | 0.3
BR - 16 | Spare Number
BR - 17 | Under Counter Glass Washer | 450 x 575 x 700 | 1 | Electrolux | NGWDPDD |  | 3.5 | 3.5 | I |  | 12 |  | 100 | [9 empty] | 3.5
BR - 18 | Lockable Storage Cupboard | 450 x 600 x 950 | 1 | Interior Designer Scope
| TOTAL | [20 empty] | 1.273 | 3.5 | 3.6
8.373