## Total Load
Date | :30.01.2024 / R1
Project | : Chai Point @ Hyderabad International Airport(HIAL)
Consultants
Subject | : Electrical Load Estimate
Total Electrical load
Sl.No | Description | Area in Sq.ft | Particulars | Connected Load | Diversity | Maximum Demand | Maximum Demand
|  |  |  | in KVA | Factor | in KVA | in kW
1 | Lighting (As per ltg lyt) |  |  | 0.14824 | 0.8 | 0.11859 | 0.1008
2 | Workstation loads |  |  | 1.21 | 0.9 | 1.089 | 0.92565
3 | HVAC |  |  | 1.3 | 0.6 | 0.78 | 0.663
4 | Kitchen |  |  | 30.605 | 0.6 | 18.363 | 15.6085
5 | Spare |  |  | 0.2 | 0.6 | 0.12 | 0.102
| Total |  |  | 33.4632 |  | 20.4706 | 17.4
| Connected load in kW = |  | 28.4437
| Connected load in kVA= |  | 33.4632
| Maximum Demand in kVA= |  | 20.4706
| Maximum Demand in kW= |  | 17.4

## Workstation load
Date | :30.01.2024 / R1
Project | : Chai Point @ Hyderabad International Airport(HIAL)
Consultants
Subject | : Workstation load details
UPS LOAD MATRIX
SL.NO. | DESCRIPTION | UNIT LOAD IN VA | QTY | C.L IN kVA | D.F | M.D IN kVA
NON CRITICAL LOADS
1 | Computer | 120 | 1 | 0.12 | 1 | 0.12
2 | Printer | 100 | 1 | 0.1 | 1 | 0.1
3 | POS Machine | 200 | 1 | 0.2 | 1 | 0.2
4 | Scanner | 50 | 1 | 0.05 | 1 | 0.05
5 | Emergency Lighting | 18 | 5 | 0.09 | 1 | 0.09
6 | LED SCREEN | 100 | 1 | 0.1 | 1 | 0.1
7 | CCTV Panel | 150 | 1 | 0.15 | 1 | 0.15
8 | FAPA Panel | 150 | 0 | 0 | 1 | 0
9 | Music system | 200 | 0 | 0 | 1 | 0
10 | Signage | 100 | 2 | 0.2 | 1 | 0.2
11 | Network box | 100 | 1 | 0.1 | 1 | 0.1
12 | Sockets For Charging | 50 | 2 | 0.1 | 1 | 0.1
13 | Sockets For diffuser and pest flash | 50 | 0 | 0 | 1 | 0
| Sub Total - Non-Critical load |  |  | 1.21 |  | 1.21
| UPS sizing @ 80% loading for non-critical load + Critical load |  |  |  |  | 1.4235
| Recommended UPS rating with 15mins back-up |  |  | 2 kVA

## Lighting
Date | :30.01.2024 / R1
Project | : Chai Point @ Hyderabad International Airport(HIAL)
Consultants
Subject | : Lighting load details
LIGHTING LOAD
SL.NO | Light Fixture Description | No of fixtures | Wattage | Total Load
1 | Ceiling mounted light | 7 | 18 | 126
2 | Track light | 0 | 20 | 0
3 | Pendant light | 0 | 20 | 0
4 | Fan Chandlier/Lights | 0 | 50 | 0
5 | Light Box with 18W LED 4ft Light (each side 2 set) | 0 | 18 | 0
| TOTAL LOAD (Kw) |  |  | 0.126

## Kitchen Equipments
Date | :30.01.2024 / R1
Project | : Chai Point @ Hyderabad International Airport(HIAL)
Consultants
Subject | : Kitchen equipments load details
S.No | ITEM | QTY | UNIT | Power supply | Load in Watts | Total Watts | Total KW
1 | Microwave Oven | 2 | nos | 1∅ | 1000 | 2000 | 2
2 | Griller | 2 | nos | 1∅ | 2000 | 4000 | 4
3 | Induction Pad | 0 | nos | 1∅ | 2000 | 0 | 0
4 | Blender | 2 | nos | 1∅ | 1000 | 2000 | 2
5 | SS Chiller | 2 | nos | 1∅ | 850 | 1700 | 1.7
6 | Visi cooler | 0 | nos | 1∅ | 850 | 0 | 0
7 | Pradeep- Heated Electric Urns | 2 | nos | 1∅ | 2400 | 4800 | 4.8
8 | HMHW Machine | 0 | nos | 1∅ | 3000 | 0 | 0
9 | Food Display Unit | 1 | nos | 1∅ | 950 | 950 | 0.95
10 | Geyser 6ltr | 1 | nos | 1∅ | 2000 | 2000 | 2
11 | RO Machine 50ltr | 1 | nos | 1∅ | 45 | 45 | 0.045
12 | Music System | 0 | nos | 1∅ | 400 | 0 | 0
13 | Ice Cube Machine | 1 | nos | 1∅ | 450 | 450 | 0.45
14 | Exaust Fan | 1 | nos | 1∅ | 650 | 650 | 0.65
15 | Ceiling/Wall Fans | 0 | nos | 1∅ | 100 | 0 | 0
16 | Dish Washer | 0 | nos | 1∅ | 1800 | 0 | 0
17 | TV Screens | 0 | nos | 1∅ | 30 | 0 | 0
18 | Merry Chef | 1 | nos | 3∅ | 2200 | 2200 | 2.2
19 | Chest Freezer | 0 | nos | 1∅ | 750 | 0 | 0
20 | Fly catcher | 1 | nos | 1∅ | 60 | 60 | 0.06
21 | Coffee Machine | 1 | nos | 1∅ | 3000 | 3000 | 3
22 | Fryer | 0 | nos | 1∅ | 2500 | 0 | 0
23 | Raw power | 2 | nos | 1∅ | 50 | 100 | 0.1
24 | SS Freezer | 1 | nos | 1∅ | 650 | 650 | 0.65
25 | Open Fridge | 0 | nos | 1∅ | 650 | 0 | 0
26 | Chai Machine | 2 | nos | 1∅ | 3000 | 6000 | 6
TOTAL | [6 empty] | 30.605