## Summary
SUMMARY of Bikanervala
Sno. | Work | Amount | Tax | Total
1 | Civil & Interior | 0 | 0 | 0
2 | Electrical | 0 | 0 | 0
3 | Plumbing | 0 | 0 | 0
4 | HVAC | 0 | 0 | 0
| GRAND TOTAL |  |  | 0

## C&I
Civil & Interior BOQ
EKLERA - Foodcourt-MP - Bikanervala |  |  |  | BOQ
SR.NO. | ITEM | DESCRIPTION | UNIT | Quantity | RATE | AMOUNT
1 | Kitchen equipments unloading/ shifting | Unloading/Shifitng/ fixing of kitchen equipments. | JOB | 1 |  | 0
2 | Brick Work | Providing and constructing 115mm class A brick masonry in cement mortar 1:4 , Job to include raking out joints, scaffolding, making openings walls, curing etc. in substructure and superstructure to its true line & level in cement mortar proportion as specified in all shapes, size, at all heights, depths, leads & locations etc. complete. The rate shall also include for cleaning of surface, hacking of RCC surface in contact with brickwork, racking of joints, providing, erecting, & dismantling steel scaffolding , curing for 10 days, including 75 mm thk. R.C.C. stiffener at approximately every 1000 mm ht. with required M.S. reinforcement bars and Lintels for Doors and wall openings etc. compete as per the drgs., details & specifications. Full Height in Kitchen Area. | Sq.Ft | 1200 |  | 0
3 | Internal Plaster | P&A of single coat backing plaster of 15-18 mm thick in CM 1:4 proportion to the walls & others surface including scaffolding, curing the joints, etc. The rates are inclusive of providing chicken mesh of 18mm gauge & 150mm width at junction of brick & RCC etc. at the walls, columns, beams etc., seven days water treatment as anti crack of plaster. Complete as per site engineer's instruction. | Sq.Ft | 2500 |  | 0
|  | Using 100mm thk full ht ( Up to ht. 4800 mm) |  |  |  | 0
4 | PCC Work | Providing and laying up to 50-75 mm thick cement concrete flooring with 1:2:4 cement concrete laid to proper level and slope in alternate bays including compactions, filling joints, or as directed, finishing smooth with cement Mortar 1:1 of sufficient minimum thickness to give a smooth & even surface and curing etc. complete as per architects instructions. | Sq.Ft | 0 |  | 0
5 | IPS Work | Providing and laying cement concrete flooring 25 - 40 mm thick , C.M. 1:3 laid to proper level and slope cost should including compaction as directed and curing complete in all respect. | Sq.Ft | 0 |  | 0
6 | COBA Work | CINDER BLOCK COBA of Avg. thickness mentioned below; After laying of soil pipes, floor traps is completed the floor of the sunken portion shall be covered with cinder coba embedded manually with 15-20 mm wide joints in 20 mm thk. Waterproofing mortar 1:4 ( 1 cement : 4 coarse sand )in layers upto the full ht. of sunken portion, having top layer of 50 mm thk waterproof mortar 1:4 ( 1 cement : 4 coarse sand ) using specialized W.P. chemical, finished smooth / rough with floating coat of neat cement all complete and as per specification.-Kitchen at 250mm | Sq.Ft | 100 |  | 0
7 | KOTA skirting | Fixing & laying of 100mm high kota stone for skirting with bedding of appropriate approved make adhesive & colour joint filler inclusive of making all groove/chamfering/rounding/hole where ever required, in proper line and level in all direction, polishing/finishing/cleaning etc. Complete as per detail drawing, specification and as directed by PMC. | RFT | 170 |  | 0
8 | SS Corner Guard | P&F of 304 grade 3mm thick SS Corner guard (30mm x 30mm), mat finished as per approved sample) fixing with SS full thread screws on each corner of the kitchen's wall before cladding of tiles, so that the corner may be protected from the damages. Complete in proper line & level and site engineer's instruction. | RFT | 120 |  | 0
9 | Metal Ceiling | Fitting of false ceiling consisting of 20g Aluminium planks made of pre- coated ( Top & Bottom ) & Size : 600mmx600mm tiles . False Ceiling with necessary supports , hangers etc. provided to install light fitting , fresh air grill etc. ( from Hunter Douglas or Armstrong ) |  |  |  | 0
|  | In BOH | SFT | 450 |  | 0
10 | Dry Store Room Door | Providing & fixing in position Double Leaf Door made up of 38mm thick commercial flush door shutter of approved make & thickness, Inner sidefinished with veneer and outer side with fluted veneer finish including providing & fixing 12 mm thk Wooden lipping all around, including P/F of Door frame made out of CP Teak / Ash wood or equivalent with melamine polish finish. Size of the frame approximate 175mm wide X 50mm thick. Applicable hardware's such as s/s handles, floor spring and any other hardware etc required to complete the related works as per design & detail. door hardware make consider Dorma / Hafele/Ozon /equilient | NOS | 0 |  | 0
11 | Back Entry Door | Providing & fixing in position Single Leaf Door made up of 38mm thick commercial flush door shutter of approved make & thickness, Inner sidefinished with veneer and outer side with fluted veneer finish including providing & fixing 12 mm thk Wooden lipping all around, including P/F of Door frame made out of CP Teak / Ash wood or equivalent with melamine polish finish. Size of the frame approximate 175mm wide X 50mm thick. Applicable hardware's such as s/s handles, floor spring and any other hardware etc required to complete the related works as per design & detail. door hardware make consider Dorma / Hafele/Ozon /equilient, with vision panel (if required). | NOS | 2 |  | 0
| Front Counters: |  |  |  |  | 0
12 |  | Counter top (800mm wide) -800mm wide 19mm thick double plywood top made of approved make, bwr grade backing as directed in detail drawing. -plywood top to be fixed on the existing low height wall's -Counter top to be finished with 12mm approved shade corian |  |  |  | 0
|  | b. Outlet: Bikanervala | RFT | 10 |  | 0
13 |  | Bulkhead paneling- Front (8230mm wide) -Providing and fixing 19mm thick plywood of approved make. -Cost includes of making a 50mm thick Aluminium frame at periphery C/C Horiozontaly and vertically to maintain gap between wall and panel as directed in detail drawing |  |  |  | 0
|  | a. Outlet: Bikanervala | SFT | 40 |  | 0
| Back Counter |  |  |  |  | 0
14 |  | Counter top (700mm wide) -700mm wide 19mm thick double plywood top made of approved make, bwr grade backing as directed in detail drawing. -plywood top to be fixed on the existing low height wall's -Counter top to be finished with 12mm approved shade corian |  |  |  | 0
|  | a. Outlet: Bikanervala | RFT | 0 |  | 0
| Flooring & Cladding | Flooring & Cladding |  |  |  | 0
15 | Kota Flooring | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : 25 mm thick | SFT | 650 |  | 0
16 | Wall Tile Cladding -1 (MOH area) | Providing and fixing in sada tile of approved make & shade on any surface as per details in drawing and Over 12 mm thk bed of cement mortar 1:3 (cement : fine sand ) with thick grey cement slurry, with hairline joints using epoxy grout and providing and fixing of golden colour aluminium t-section of 25mm face. The job including cutting of tiles & making smooth edges wherever required. Rate of water jet cutting included. The work shall also include cost of materials, wastages, labour, all lead and lift at all levels, loading and unloading, transportation, curing etc. and all other incidental charges etc. Complete as specified in the drawing & to the satisfaction of the Site Engineer. GVT wall tile (Printed) With customize line work Make : -VARMORA code name CARARA ENZO in exposed area. | SFT | 250 |  | 0
17 | Sada Wall Tile Cladding -2 (Kitchen & BOH area) | Providing and fixing in sada tile of approved make & shade on any surface as per details in drawing and Over 12 mm thk bed of cement mortar 1:3 (cement : fine sand ) with thick grey cement slurry, with hairline joints using epoxy grout. The job including cutting of tiles & making smooth edges wherever required. Rate of water jet cutting included. The work shall also include cost of materials, wastages, labour, all lead and lift at all levels, loading and unloading, transportation, curing etc. and all other incidental charges etc. Complete as specified in the drawing & to the satisfaction of the Site Engineer. Ceramic wall tile (Plain tiles) Make : Kajaria/Varmora/ Nittco/Somany/ Ceramic wall tile white/ Satin white 300x450mm below counter or hidden area | SFT | 1450 |  | 0
| False Ceiling | False ceilling |  |  |  | 0
18 | Gypsum false ceiling (MOH area) | Gypsum Board false Ceiling: Providing, fabrication and fixing in position of false ceiling ( height will be decided on the spot as per site conditions) by fixing 12 mm Th. Gypsum Board sheets on frame work of GI sheet section. The main runners of 22 gauge GI sheet and cross runners of 24 gauge GI sheet must be framed to form a mesh of 2’0”x2’0” c/c. The Gypsum Board must be fixed to the GI frame and joint to be properly filled in with POP paste and paper tape to get a leveled smooth ceiling. Recessing of the Gypsum Board for light fixtures must be done along with extra frame work of GI sheet section to hold the concealed light fixtures etc. directed by the site engineer. Including two coats of primer suitable for gypsum board two or more coats of plastic emulsion paint of approved shade and also including making necessary openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitable fixed all complete as per drawing and specification and direction. Rate to be inclusive of shadow profile at the junction of wall & ceiling, in between of ceiling, etc. complete.-MOH Area | SFT | 200 |  | 0
| Carpentry Works | Carpentry Work |  |  |  | 0
19 | Front Undercounter Storage | Under counter units to be finished with plain laminate (Merino/Greenlam/Equivalent) internally with provision of shelves and drawers for storage. All ply edges to be bounded with matching laminate. 18mm thk. Shutter to be made of plyboard (Century/Greenply/Equivalent) finished in app. Laminate (Merino/Greenlam/Equivalent) from outside as per schedule. | Nos. | 1 |  | 0
length - 1090mm. Depth - 800mm, height - 1050mm
| * | Providing & Fixing of softwood framework within the counter panelling as per detail.
| * | Provision and fixing of all hardware, channels, box hinges (Hettich/hafele/equivalent), locks (Hettich/hafele/godrej/equivalent) etc.
| * | Providing & fixing of 100mm high & 2mm thk. Brushed Finish SS skirting.
| * | Contractor to coordinate with electrical contractor for fixing of switch & sockets.
20 | Back Undercounter Storage | Under counter units to be finished with plain laminate (Merino/Greenlam/equivalent) internally with provision of drawers & shelves for storage. All ply edges to be bounded with matching laminate & 18mm thk shutter to be made of plyboard (Century/Greenply/equivalent) finished in app. Laminate (Merino/Greenlam/equivalent) from outside as per schedule . | Nos. | 0 |  | 0
length - 4600mm. Depth - 750mm, height - 1000mm
| * | Provision and fixing of all hardware, channels, box hinges (hettich/hafele/equivalent), locks (hettich/hafele/godrej/equivalent) etc.
| * | Providing & Fixing of 100mm high & 2mm thk. S.S. plate skirting at the bottom.
21 | FLOOR TRANSITION STRIP | Providing & fixing 20-25mm wide 'T' shape gloden colur brush finish Transition strip | RFT | 10 |  | 0
22 | WATERPROOFING | Providing and laying a proprietary chemical waterproofing system consisting of polymer-modified acrylic base coating in two coats in form of a slurry (total consumption of 1.5 Kg/Sqm) as approved by the PM and as directed by the approved manufacturer of waterproofing coating, with sandwiched fiber mesh and protective screed. The work shall include cleaning the surface, grouting porous surfaces making ‘V’ grooves at junctions, cracks with nonshrink crystalline base cementitious grout, etc. Further including horizontal and vertical surfaces protected with 20mm screeding in 1:4 mortar (1 cement: 4 sand), finished in ready to receive Architectural finish, in the correct line, level, and plumb, curing, grouting, testing, etc. all complete to the entire satisfaction of the PM. | Sq.ft. | 0 |  | 0
23 | Pest control at site | Providing Pest Control & Anti-termite treatment by appointing a specialized agency as per the specifications mentioned by the Bureau of Indian Standard & Agencies specification ( Whichever is higher ) for General Civil , Plumbing / Drainage & timber / Carpentry works , Gypsum related work including 5 Years guarantee under suitable undertaking on stamp paper etc complete as directed . ( Mode of Measurement to be on carpet area of floor & not the area of surface treated.) | Sq.ft. | 650 |  | 0
24 | Toughnened Glass | P/F 12 mm thk. toughened glass for sneeze gaurd including all necessary required hardware fitting and handles, floor spring and any other hardware etc required to complete the related works as per design & detail. door hardware make consider Dorma / Hafele/Ozon /equilient | Sq.ft. | 50 |  | 0
25 | Window/ door jamb | Providing & Fixing polished Jet black granite stone /Approved stone in "Z" Door Jambs, Window Cills, Architrave, ledge wall top etc. (maximum width upto 300mm) in cement mortar 1:3 & in cement slurry, including necessary filing joints in white cement pigmented to approved shade. Also includes necessary edge polishing, champhering, moulding etc complete as per the direction of TFS. Basic Rate of Black Granite : Rs 150/- per Sft. (Granite shall be Procured by Contractor) | Sq.ft. | 50 |  | 0
26 | HEAVY M.S Work & Framework | Providing, fabricating & erection of Steel work in built up section/ framed work i/c cutting, welding, hoisting, fixing in position & applying a priming coat of approved steel primer using steel etc, as required. In structure slab (ISMB, ISMC etc.) or stringers, treads, landing of stair case i/c use of chequered plate wherever required, all complete. Including primer and 2 coat paints, For 200 liters of water tank and HVAC units platform - Including Awing of polycarbonate sheet for RO and other areas | KG | 550 |  | 0
0

## Electrical
EKLERA FOOD COURT
Panels & Distribution Board |  |  | BOQ
OUTLET-2 BIKANERWALA
SR. NO. | DESCRIPTION | UNIT | QTY | RATE | TOTAL BOQ AMOUNT
1 | PANELS, SWITCHGEARS & DISTRIBUTION BOARD
1.1 | MAIN PANEL-1 | Nos.
Incomer : 63 AMPS 4P MCCB, 25kA with TM Based O/C & SC Release.
Meter & Protection: ELR with CBCT; 60/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 100A TPN Cu Busbar
Outgoings:
a) 63A 4P MCCB, 16kA, TM BASED-1 Nos.
d) 40A DP MCB-2 Nos.
f) 32A 4P MCCB 16kA TM Based Releases with 1.5 kW DOL Starter, Phase Indicating lamps, ON/OFF/TRIP Indication, ON/OFF Push Button-1 Nos.
1.2 | MAIN PANEL-2 | Nos.
Incomer : 40 AMPS 4P MCCB, 25kA with TM Based O/C & SC Release.
Meter & Protection: ELR with CBCT; 40/5A, 15VA, CL-1 CT's -3 Nos. for Schneider make Digital Load Manager (EM 6400 NG)
Indication: Phase indicating lamps with 6A MCB
Busbar: 75A TPN Cu Busbar
Outgoings:
a) 32A 4P MCB, 10kA-1 Nos.
b) 25A 4P MCB, 10kA-1 Nos.
c) 32A DP MCB, 10kA-1 Nos.
d) 40A DP MCB, 10kA-1 Nos.
2 | SWITCHGEARS & DISTRIBUTION BOARD
Supplying & installing at site in positioning, connecting, testing and commissioning of the following type Distribution Boards & Switchgears. (IP-43) ACRY DB
Provide insulated dedicated earth link for UPS DB
All MCB's for UPS shall be D Curve, C Curve for Power & B Curve for Lighting.
2.1 | SWITCHGEARS
2.1.1 | Supply, installation, testing and commissioning of sheet metal enclosures for the following switchgears.
2.1.1.a | 63/40/32/20 amps 4P MCB 'C' TYPE with complete with all mounting accessories – for Indoor Legrand make | Nos. | 1 |  | 0
2.1.1.b | 63/40/32/20 amps DP MCB 'C' TYPE with complete with all mounting accessories – IP-65 |  | 0 |  | 0
2.1.1.c | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 2 |  | 0
2.1.1.d | 25 amps DP MCB with 25A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 0 |  | 0
2.1.1.d | 16 amps DP MCB with 15A 3 Pin Ray Roll Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 15 |  | 0
2.1.1.e | 5/15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 10 |  | 0
2.2 | DISTRIBUTION BOARDS |  |  |  | 0
2.2.1 | 6 WAY SPN DB - UPS DB | Nos. | 1 |  | 0
| Incomer : 20 AMPS DP MCB 10KA : 1 Nos. |  |  |  | 0
| Outgoings : 6/10/16 A SP MCB "B" Type - 4 Nos. |  |  |  | 0
2.2.2 | FABRICATED - LPDB | Nos. | 1 |  | 0
| Incomer : 80A, FP, MCB, 10kA: 1 Nos |  |  |  | 0
| Sub Incomer : 63A, DP, RCCB, 100mA: 3 Nos |  |  |  | 0
| Outgoings : 10/16/20/25 A SP MCB "C" Type - 36 Nos. |  |  |  | 0
| Outgoings : 32 A SP MCB "C" Type - 1 Nos. |  |  |  | 0
2.2.3 | 12 WAY SPN DB - UPS DB | Nos. |  |  | 0
| Incomer : 32 AMPS DP RCBO 100mA |  |  |  | 0
| Outgoings : 10/16/20 A SP MCB "C" Type - 6 Nos. |  |  |  | 0
| TOTAL FOR DISTRIBUTION BOARDS |  |  |  | 0
2 | MV CABLES |  |  |  | 0
2.1 | POWER CABLING |  |  |  | 0
| Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE FRLS armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications. |  |  |  | 0
2.1.1 | Aluminium cables |  |  |  | 0
a | 4C x 50 Sq.mm. | Mtr. | 10 |  | 0
b | 3.5C x 35 Sq.mm. | Mtr. | 5 |  | 0
c | 4C x 25 Sq.mm. | Mtr. | 25 |  | 0
2.1.2 | - do - but for copper cables |  |  |  | 0
a | 4C x 25 Sq.mm. | Mtr. |  |  | 0
b | 4C x 16 Sq.mm. | Mtr. |  |  | 0
c | 4C x 10 Sq.mm. | Mtr. |  |  | 0
d | 4C x 6 Sq.mm. | Mtr. |  |  | 0
e | 4C x 4 Sq.mm. | Mtr. |  |  | 0
f | 4C x 2.5 Sq.mm. | Mtr. |  |  | 0
g | 3C x 6 Sq.mm. | Mtr. |  |  | 0
h | 3C x 4 Sq.mm. | Mtr. |  |  | 0
i | 3C x 2.5 Sq.mm. | Mtr. |  |  | 0
2.1.3 | CU Flexible Cables |  |  |  | 0
a | 4C x 6 Sq.mm. | Mtr. |  |  | 0
b | 4C x 4 Sq.mm. | Mtr. |  |  | 0
c | 3C x 4 Sq.mm. | Mtr. |  |  | 0
d | 3C x 2.5 Sq.mm. | Mtr. |  |  | 0
e | 2C x 2.5 Sq.mm. for Earthing | Mtr. |  |  | 0
2.1.4 | , - do - but for copper flexible cables |  |  |  | 0
a | 1c x 4 Sq.mm PVC insulated PVC flexible copper conductor cables alongwith termination (GREEN COLOUR) | Mtr. |  |  | 0
| TOTAL FOR POWER CABLES |  |  |  | 0
2.2 | CABLE TERMINATION |  |  |  | 0
| Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper. |  |  |  | 0
a | 4C x 50 Sq.mm. AL | Nos. | 1 |  | 0
b | 3.5C x 35 Sq.mm. | Nos. | 1 |  | 0
c | 4C x 25 Sq.mm. | Nos. | 1 |  | 0
d | 4C x 16 Sq.mm. CU | Nos. |  |  | 0
e | 4C x 10 Sq.mm. | Nos. |  |  | 0
f | 4C x 6 Sq.mm. | Nos. |  |  | 0
g | 4C x 4 Sq.mm. | Nos. |  |  | 0
h | 4C x 2.5 Sq.mm. | Nos. |  |  | 0
i | 3C x 6 Sq.mm. | Nos. |  |  | 0
j | 3C x 4 Sq.mm. | Nos. |  |  | 0
k | 3C x 2.5 Sq.mm. | Nos. |  |  | 0
l | Flexible cable |  |  |  | 0
m | 4C x 6 Sq.mm. | Nos. |  |  | 0
n | 4C x 4 Sq.mm. | Nos. |  |  | 0
o | 3C x 4 Sq.mm. | Nos. |  |  | 0
p | 3C x 2.5 Sq.mm. (Lighting) | Nos. |  |  | 0
q | 2C x 2.5 Sq.mm. | Nos. |  |  | 0
| TOTAL FOR POWER CABLE TERMINATION |  |  |  | 0
3 | RACEWAYS AND CABLE TRAYS |  |  |  | 0
3.1 | TRUNKING: Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick G.I. Trunking of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick G.I. coupler plates & Reducers as per requirement. The cost shall including all supporting and fixing accessories with 8/10mm threaded Ros & Clamps etc. including dash fasteners. |  |  |  | 0
a | 100 mm (wide) x 50 mm (height) | Mtr. |  |  | 0
b | 50 mm (wide) x 50 mm (height) | Mtr. | 10 |  | 0
3.2 | RACEWAY: Fabricating, supplying to site of installation, installation in the floor before the flooring from 2 mm thick pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick. The raceways shall be clamped to the floor slab with GI clamps 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI cover which will be nut bolted to the Junction box to cover the entire Junction box side walls complete as required etc. all the Raceways sections shall be earthed. |  |  |  | 0
a | 100 mm (wide) x 40 mm (height) | Mtr. | 10 |  | 0
b | 65 mm (wide) x 40 mm (height) | Mtr. | 0 |  | 0
3.3 | JUNCTION BOXES: Fabricating supplying to site of installation, Junction boxes made from 2 mm thick pregalvanised sheet, with 3.0 mm thick pregalvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The floor junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
| (variation in height may be considered for quoting as floor thickness may vary) |  |  |  | 0
a | 250 mm x 250 x 60/50 mm (height) | Mtr. | 5 |  | 0
b | 150 mm x 150 x 60/50 mm (height) | Mtr. | 5 |  | 0
c | 100 mm x 150 x 60/50 mm (height) | Mtr. | 5 |  | 0
3.4 | CABLE TRAY: Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
a | 300 mm wide x 50 mm x 2.0 mm thk | Mtr. |  |  | 0
b | 150 mm wide x 50 mm x 2.0 mm thk | Mtr. | 0 |  | 0
c | 100 mm wide x 50 mm x 2.0 mm thk | Mtr. | 20 |  | 0
d | 50 mm wide x 50 mm x 2.0 mm thk | Mtr. | 10 |  | 0
| TOTAL FOR RACEWAYS AND CABLE TRAYS |  |  |  | 0
4 | POINT WIRING |  |  |  | 0
| Point wiring LENGTH from DB to SB or First Light point control be MCB shall be avg. of 15Mtr. of 3C x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires. For SB to SB the length shall be measured in Mtr. |  |  |  | 0
| The secondary/Loop point length shall be 10Mtr from Light fixture to light fixture. If secondary point shall be operated from MCB then the length shall be 10 Mtr. |  |  |  | 0
| All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| The Length shall be paid as per the actual measurements & as per following manner. |  |  |  | 0
4.1 | Wiring for the Primary light points with 3C x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted from Distribution Board to Switch Board including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates shall exclusive of Switches & Switch boxes. |  |  |  | 0
4.1.1 | From DB to Normal Switch Board | Mtr. | 200 |  | 0
4.1.2 | From DB to Emergency Switch Board | Mtr. | 100 |  | 0
4.2 | Wiring for the following light points with 3 x 2.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in GI conduits in F.ceiling/walls/ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required from the above switch board. Rates shall exclusive of Switches & Switch Box. (FROM SB TO LIGHT) |  |  |  | 0
4.2.1 | First point controlled by one no. 6 amp switch. (upto 10Mtr.) | Nos. | 8 |  | 0
4.2.2 | First point controlled by one no. 6 amp switch. (upto 20Mtr.) | Nos. | 4 |  | 0
4.2.3 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 10Mtr.) | Nos. | 8 |  | 0
4.2.4 | First point controlled by one no. 6 amp switch. For Emergency Light (upto 20Mtr.) | Nos. | 3 |  | 0
4.3 | Same as item No. 4.2.1 & 4.2.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. | 0 |  | 0
4.4 | Same as item No. 4.2.3 & 4.2.4 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed GI conduit and earthing For Emergency Light | Nos. | 0 |  | 0
4.5 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3C x 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed GI conduits as called for and earthing. |  |  |  | 0
4.5.1 | First point controlled by existing MCB in D.B. | Mtr. |  |  | 0
4.5.2 | First Emergency point controlled by existing MCB in D.B. | Mtr. |  |  | 0
4.6 | Same as item No.4.5.1 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed GI conduit and earthing | Nos. |  |  | 0
4.7 | Same as item No. 4.5.2 above but LOOP POINT i.e. wiring of point looped from first point with 3C x 2.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing For Emergency Lighting | Nos. |  |  | 0
4.8 | Wiring for UPS/Raw plug outlets points with 3C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. | 50 |  | 0
4.9 | Wiring for UPS/Raw plug outlets points with 4C x 4 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | Mtr. |  |  | 0
4.1 | Providing and fixing in position the following GI RIGID conduits including all accessories concealed in F. ceiling/wall/floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
4.10.1 | 20 mm dia GI Conduit | Mtr. |  |  | 0
4.10.2 | 25 mm dia GI Conduit | Mtr. | 200 |  | 0
4.11 | Providing and fixing in position the following GI FLEXIBLE conduits including all accessories concealed in F. ceiling/wall/floor as required including pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
4.11.1 | 20 mm dia GI Conduit | Mtr. |  |  | 0
4.11.2 | 25 mm dia GI Conduit | Mtr. | 50 |  | 0
0
4.12 | Supply & Laying of 2Cx2.5 Sq.mm FRLS Cu Flexible Cable in 25mm dia. GI Conduit for CCTV | Mtr. | 70 |  | 0
| TOTAL FOR POINT WIRING |  |  |  | 0
5 | MODULAR SWITCHES
5.1 | Supply, installation, testing & commissioning of following types of modular switches, cover plates, 5 sided G.I. Boxes for housing the modular switches & earthing complete as required. GI Boxes to have earth pin for body earthing. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.(Make- Legrand Aretor Series)
5.1.1 | 6A One Way Switch | Nos. | 5 |  | 0
5.1.2 | 6A 5 pin Socket - 1Nos. & 6A Switch - 1Nos. | Nos. | 1 |  | 0
5.1.3 | 6/16A Socket outlet - 1Nos. & 16A Switch - 1Nos.(Raw/UPS Power) | Nos. | 20 |  | 0
5.1.4 | 5/15 amps Switch Socket complete with all mounting accessories waterproof (IP-65) for Kitchen | Nos. | 10 |  | 0
5.1.5 | 20 Amp 1- Ph Industrial Socket (Metal Clad) | Nos. | 0 |  | 0
5.1.5 | 32 Amp 3- Ph Industrial Socket (Metal Clad) | Nos. | 1 |  | 0
5.1.6 | 20 Amp 1- Ph Electrical Outlet | Nos. | 0 |  | 0
5.1.7 | Data Outlet (RJ-45) | Nos. | 7 |  | 0
5.1.8 | Telephone Outlet (RJ-11) | Nos. | 1 |  | 0
| TOTAL FOR MODULAR SWITCHES |  |  |  | 0
6 | GENERAL EARTHING |  |  |  | 0
6.1 | Supplying and erecting following GI strip used for earthing on wall with necessary MS clamps fixed on wall/Cable trays/Hume pipes etc. The jointes shall be Bolted/Welded. The joints shall be painted with bituminous paint in an approved manner. |  |  |  | 0
6.1.1 | 25 x 3 mm | Mtr. |  |  | 0
6.2 | Supplying and erecting bare Copper conductor of following sizes |  |  |  | 0
6.2.1 | 8 SWG | RMtr. | 50 |  | 0
| TOTAL FOR GENERAL EARTHING |  |  |  | 0
7 | LIGHT FIXTURES INSTALLATION
7.1 | Receiving from Store, Installation, testing & commissioning of following light fixtures with complete installation hardwares including Anchor fastner, supporting Hook/Rods as per final approval from Architect/Client/Consultant |  |  |  | 0
7.1.1 | ROUND CEILING LIGHT 10w-20w - 3000kelvin | Nos. | 10 |  | 0
7.1.2 | 600x600 square LED panel lights 36w - 6000kelvin | Nos. | 12 |  | 0
7.1.3 | HANGING LIGHT | Nos. |  |  | 0
7.1.4 | TRACK LIGHT | Nos. |  |  | 0
7.1.6 | LED STRIP (15 M) | Mtr. |  |  | 0
7.1.7 | T5 LED WALL LIGHT 28w- 6000kevin | Nos. | 4 |  | 0
8 | MISCELLANEOUS WORKS
8.1 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. |  |  | 0
8.2 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. |  |  | 0
8.3 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical & ELV Services executed at site. | Part of Tender |  |  | 0
8 | CCTV System |  |  |  | 0
8.1 | Supply Installation, testing & commissining of Indoor type Analogue Dome Camera with 1/2" 2 Mega Pixel, integrated 4/6mm Fixed lens, Full HD high definition, Inbuilt Smart IR LED upto 10m distance, 0.02 lux color/0 lux with IR LEDs on, H.264, H.265 high profile, True Day/Night, , & 12VDC operated, ONVIF compliant, with Junction box & required accessories. | Nos. |  |  | 0
8.2 | Supply, installation, testing & commissioning of 16 Channel Licence Server & hardware based Digital Video Recorder (DVR) with 3 Client licence, Embedded OS & per-loaded video recording software, Minimum 256 Mbps incoming bandwidth and 256 Mbps outgoing bandwidth, 1x 1000Mbps Ports, ONVIF, H.265 high profile, 2 x HDMI & VGA output for monitor, Upto 40TB storage capacity, minimum 4 SATA Interfaces, upto 10TB capacity for each SATA, including 20TB Storage HDD (Hard Disk) @ recording resolution of 25fps @ 1080P and H.265 for 30 days, including required accessories. Vendor to submit Bandwidth & Storage calculation sheet. | Nos |  |  | 0
8.3 | Supply, laying, testing of RG 6 Cable for CCTV. | Mrt | 250 |  | 0
8.4 | Supply, laying, testing (for continuity) of 23 AWG Copper, Cat 6 UTP Cable, Data & Wi-Fi points including end termination, dressing, bunching of cables with identification ferruling. | Mrt | 200 |  | 0
9 | Fire Detection and Alarm System |  |  |  | 0
9.1 | Supply, installation, testing & commissioning of Conventional Type optical Smoke Detector with inbuilt scattered light measurement, rate of rise and fixed temperature based technology and LED indication should be on the centre of the detector with mounting base complete as required. | No. | 6 |  | 0
9.2 | Supply, Installation, testing & commissioning of addressable type smoke Detector with floating sensitivity Complete with all accessories like base, base box, etc. to be installed under / above false ceiling, roof and concealed space, etc. complete as required. | No. | 0 |  | 0
9.3 | Supply, Installation, testing & commissioning of addressable type Heat Detector (fixed cum-rate of rise type) with fix temperature at 78 o C complete with all fixing accessories like base, base box, etc to be installed under /above false ceiling, roof and concealed space, etc complete as required. | No. | 2 |  | 0
9.4 | Supply, installation, testing & commissioning of conventional Manual Call Point (break glass type)complete with push button,enclosed in box with provision of conduit/cable coupling.The unit to be painted fire red outside ,white inside and written "in case of fire break glass" or as required. | No. | 1 |  | 0
9.5 | Supply, Installation, testing & commissioning of addressable type manual call point (break glass type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and written 'In case of fire break glass'. | No. | 0 |  | 0
9.6 | Supply, installation, testing & commissioning of Conventional Hooter cum Strobe complete as required.110 cd light & 85 dB adjustable at different locations complete with all fixing accessories etc under false ceiling ,roof,wall etc complete as required. | No. | 1 |  | 0
9.7 | Supply, Installation, testing & commissioning of hoooters (Specification :- 110 cd light & 85 dB with adjustable DB) at different locations complete with all fixing accessories, etc under false ceiling roof, wall etc. complete as required. | No. | 0 |  | 0
9.8 | Supply, installation, testing & commissioning of 2 zone based conventional Fire alarm control panel with standard set complete as required. | Set | 1 |  | 0
9.9 | Supplying, erecting, testing and commissioning the addressable type Fire Alarm Control Panel (FACP) with standard accessories complete | Set | 0 |  | 0
9.1 | Supplying and erecting PVC armoured cable 2 core 1.5 sq. mm FRLS copper conductor complete erected on wall / celling as per specification | Mtr. | 50 |  | 0
9.11 | Supply installation testing and comissioning of Hood supression system(Ceasefire or equivalent). | No. | 0 |  | 0
0
0

## Plumbing
EKLERA FOOD COURT
DRAINAGE & WATER SUPPLY WORK BOQ |  |  | BOQ
BIKANERWALA
Srl No. | Description | Unit | Qty | Rate | Amount
A | WATER SUPPLY PIPING
1 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes SDR 11, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. (Concealed work including cutting chases and making good the walls etc.,) Pressure Testing (Pipe shall be tested with 1.5 times working pressure as covered in specifications)
1.1 | 15 mm Dia | R.mt |  |  | 0
1.2 | 20 mm Dia | R.mt | 50 |  | 0
1.3 | 25 mm Dia | R.mt | 20 |  | 0
1.4 | 32mm Dia | R.mt | 15 |  | 0
2 | Providing & fixing gun metal lever operated ball valve. Tested to a pressure of 15 Kg / Sqcm. Including flanges/union, nuts, bolts, washer etc. Complete as required. |  |  |  | 0
2.1 | 20mm Dia | Nos. |  |  | 0
2.2 | 25mm Dia | Nos. | 2 |  | 0
2.3 | 32mm Dia | Nos. |  |  | 0
2.4 | 40mm Dia | Nos. |  |  | 0
3 | Providing, fixing, testing and commissioning of NRV with forged brass body, brass diaphram and SS seal in water supply pipes. Complete as required. |  |  |  | 0
3.1 | 25mm Dia | Nos. |  |  | 0
4 | Providing, fixing, testing and commissioning of Y STRAINER FLANGED END EPOXY COATED WITH SS SCREEN (CR16B) |  |  |  | 0
4.1 | 25mm Dia | Nos. |  |  | 0
5 | Providing and fixing of brass multijet water meters with magnetic transmision of IS-779:1994 including with rubber gasket, flanges/ unions, nuts, bolts, washers, etc. complete as required. Make : Kranti |  |  |  | 0
5.1 | 25 mm Dia incoming line | Nos. |  |  | 0
5.2 | 32 mm Dia incoming line | Nos. |  |  | 0
5.3 | 40 mm Dia incoming line | Nos. |  |  | 0
6 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  |  |  | 0
6.1 | 5 L Capacity- | Nos. |  |  | 0
6.2 | 20 L Capacity | Nos. |  |  | 0
6.3 | 35 L Capacity- For dishwasher | Nos. | 1 |  | 0
7 | SITC of Eco smart RO 200 LPH Capacity with all required accessories | Nos |  |  | 0
8 | SITC of grease trap -model NGT-14 Capacity -25.5 lit ( 28 LPM) with all required accessories( SIZE:- | Nos |  |  | 0
9 | SITC of grease trap -model NGT-30 Capacity -47.5 lit ( 57 LPM) with all required accessories( SIZE:- | Nos |  |  | 0
B | DRAINAGE |  |  |  | 0
1 | Providing and fixing Upvc SWR pipes ( Class B Heavy Type) including all fittings (plain or door) e.g. bends, junction, cowls, offsets, access pieces, jointing with rubber ring/solvent cement joints,jali,clamps including cutting chase or holes in walls and floors and making good where required.( Inside the building) |  |  |  | 0
1.1 | 50mm Dia | R.mt |  |  | 0
1.2 | 75mm Dia | R.mt | 10 |  | 0
1.3 | 100 mm Dia | R.mt | 15 |  | 0
1.4 | 150 mm Dia | R.mt |  |  | 0
2 | Providing & fixing in position pipe trap of self cleaning design of following sizes for the embedded areas. Making proper connection with , cutting chase / hole in floors /slabs and bringing the same in proper condition in cement concrete 1:2:4 mix complete as required. including cost of cutting and making good the walls and floors where required. Make : |  |  |  | 0
2.1 | P-trap 110 mm dia | Each |  |  | 0
2.2 | Multi trap 110 mm dia with square grating (Outlet 75MM dia) | Each |  |  | 0
2.3 | Floor trap 110 mm dia with grating(Outlet 75MM dia) | Each | 8 |  | 0
2.4 | Nahani trap 110 mm dia with grating(Outlet 75MM dia) | Each |  |  | 0
C | SANITARY AND C. P. FITTINGS & FIXTURES |  |  |  | 0
| Only installation, testing and commissioning of sanitary and C.P. fittings |  |  |  | 0
1.1 | Providing and Fixing C.P. brass wall mounted/ table top sink mixer with swinging spout, wall mounted type complete as required. | Nos | 7 |  | 0
1.2 | Angle Cock with PVC pipe connection upto sink/Geyser /RO connection | Nos | 12 |  | 0
D | S.S. GRATING |  |  |  | 0
| SITC of , testing and commissioning of S.S.Gratings |  |  |  | 0
1 | Making chamber in brick work including internal tiling etc for S.S Grating size, 300mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 5 |  | 0
2 | Making chamber in brick work including internal tiling etc for S.S Grating size, 1050mm x 350mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. | Nos. | 1 |  | 0
1.1 | Providing and Fixing of S.S. sink without drain board over all size 600x450x200mm Single bowl size:- 500x400x200mm with C.P. Brass waste assembly, bottle Trap For sinks with horizontal outlet, (1 1/2" X 40mm) with extension piece wall flange & rubbre adopters complete as required. | Nos
| GRAND - TOTAL A , B, C AND D |  |  |  | 0

## HVAC
NAME OF PROJECT: Food Court at Eklera
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
A | EQUIPMENTS
1 | AIR SCRUBBER
Modular Double skin Floor mounted air scrubber units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet & 0.8mm thick Plain GI (270gsm) inner sheet comprising of Intake section for duct connection, Al Wiremesh filter section, Wet section made of 20g SS Tank, Three Phase Pump (1w+1s), GI internal piping, Single Bank Spray Nozzles and 2bend PVC eliminators. Blower section with DIDW Aerofoil/ Backward/ Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type & suitable for VFD operation) & LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual / motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates/Casing/blank offs of Eliminators shall also be made of SS.
1.1 | 6000 CFM (65mm of wg Total St. Pressure) | No. | 1 |  | 0
2 | AIR WASHER
Modular Double skin Floor mounted air washer units made of 23+2mm thick PUF insulated panels extruded aluminum hollow profiles with 0.8mm thick pre-coated GI Outer Sheet & 0.8mm thick Plain GI (270gsm) inner sheet comprising of Al Wiremesh filter section, Wet section made of 20g SS Tank, Single Phase Pump (1w+1s), PVC internal piping, Distribution system, 200mm deep Cellulose Pads & 2 bend PVC eliminators. Blower section with DIDW Aerofoil/ Backward/ Forward curved fans, drive set with V- belts, Spring type vibration isolators, wire guard on Fan section access door, fire retardant canvass connection at fan outlet, IE-2 motor (TEFC type & suitable for VFD operation) & LED lamps for blower section, limit switch for the fan section access door with a view port and damper at the outlet of unit. All dampers shall be low leakage aluminum aerofoil design and suitable for manual / motorised operation. Units exposed to open sky shall have weather proof canopy. The End Plates/Casing/blank offs of Pads & Eliminators shall also be made of SS.
2.1 | 5000 CFM (50mm of wg Total St. Pressure) | No. | 1 |  | 0
B | AIR DISTRIBUTION
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 18 G sheet | sq.m | 25 |  | 0
| 20G sheet | sq.m | 5 |  | 0
| 22G sheet | sq.m | 5 |  | 0
| 24G sheet | sq.m | 40 |  | 0
| 26G sheet | sq.m | 5 |  | 0
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 18 G sheet | sq.m | 5 |  | 0
| 20G sheet | sq.m | 5 |  | 0
| 22G sheet | sq.m | 5 |  | 0
| 24G sheet | sq.m | 5 |  | 0
3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 1 |  | 0
4 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1 |  | 0
5 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 2 |  | 0
6 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction exhaust air louvers with bird screen for exhaust air as per specifications and approved shop drawings. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 0.1 |  | 0
7 | Supply, installation, testing and balancing of Powder coated/Anodised extruded aluminium construction. inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | SQMT | 0.1 |  | 0
C | THERMAL INSULATION
1 | THERMAL INSULATION FOR KITCHEN DUCTS
SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade.
| 13 mm Thick | sq.m | 30 |  | 0
D | ELECTRICAL INSTALLATION
1 | CONTROL PANEL FOR AHU / Air washer / Scrubber (WITH DOL / SD STARTER)
Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming, earthing & terminating into MCCB in each panel shall be provided by the electrical contractor.
All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included.
All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System.
The panel shall include the following components and accessories.
a. | MCCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 20 KA.
b. | DOL / SD starter as per HP ratings
c. | Terminal block for power distribution.
d. | Contactor, over load relay with built in single phasing protection.
e. | Phase indicating lights and indicating light for ON status.
f. | Digital voltmeter and digital ammeter with selector switches.
g. | Time delay relay for delayed automatic restart of air handling unit motor.
h | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation.
i | All starters shall be provided with suitable potential free contract for connections to the Building Automation System.
The number of AHU control panels shall be as follows.
| 3 HP DOL Starter | No. | 1 |  | 0
| 5 HP DOL Starter | No. | 1 |  | 0
GRAND TOTAL |  |  |  |  | 0

## ELE APPROVED MAKES
1. LIST OF APPROVED MAKES FOR ELECTRICAL EQUIPMENT & MATERIALS
(All major equipment/Materials shall be tested and approved by CPRI/ERDA (NABL accredited laboratory) and shall carry ISI mark. All manufacturer shall possess valid ISO certificate)
Sl. No. | Equipment & materials | Makes
1 | Low voltage switchgear enclosure (415v) (iec 61439 compliant) & switchgears | Schneider / legrand / siemens / abb / l&t
2 | Ups system (uninterruptable power supply) (415/230v) | Apc-schneider /eaton / socomec / vertiv
3 | Vrla smf battery | Excide / amararaja / rocket
4 | Dbs | Legrand - ekinoxe / schneider - acti9 / siemens / abb
5 | Vfd (variable frequency drive) | Allen bradley / alstom / danfoss / siemens/ abb/ l&t yaskawa/honeywell
6 | Motor starter | Abb / schneider / siemens / l&t
7 | Cable (415v) | Rpg/ finolex / universal /havells
8 | Disconnect switch | Schneider / abb / siemens / l&t
9 | Wires/copper flexible cable | Finolex / havells / rajnigandha / rr kabel
10 | Raceways and junction boxes | Mk / legrand / obo bettermann
11 | Cable trays | Obo bettermann / legrand / indiana / profab
12 | Spd (surge arraster) | Obo / legrand / schneider
13 | Meters (analog) | Meco / rishabh / nippen / conserve / ae
14 | Meters (digital) | Ae / schneider / nippen / conserve / l&t
15 | Energy meter , load manager | Schneider (em 6400ng or equivalent) / l&t / nippen / hpl / socomec
16 | Indicating lamps | Schneider / l & t / salzer
17 | Rotary switch | Siemens / keycee / salzer / meco
18 | Push button and push button set | Siemens / schneider electric / l & t / legrand / c&s / abb
19 | Selector switch | Keycee / salzer / meco
20 | Gi conduits and accessories | Bharat / supreme/bec
21 | Control transformer [ pt / ct ] | Ashmor / kappa / elmex
22 | Fire barrier | Obo bettermann / hilti / 3m
23 | Terminal block | Essen / connect well /elmex
24 | Control switch | Alstom/kaycee/switron
25 | Hrc fuse | Siemens /l&t /alstom/s&s /cgl /ge /standard
26 | Limit switch | Siemens /essen /bch /ind syndicate/epcc(kakku)
27 | Elr with cbct | Kalpa / jvc / prok dv’s
28 | Overload relays with built in single phase preventer | Siemens/ abb/ l&t / schneider
29 | Power/aux. Contactor | L&t / schneider
30 | Auxiliary relays | Siemens / ge alstom / abb / jvs / prok dv’s
31 | Protection relay - electromagnetic type | Areva
32 | Protection relay - numeric type | Areva / siemens / l&t / sel
33 | 1.1kv, grade lt fire survival cables | Anchor/finolex/ havells / kei/ kec
34 | Signal cable | Enercon / lapp india / system tek / caliplast / eminent
35 | Cable lugs | Dowell’s / 3d / hex / jainson / comet / hmi
36 | Bimetallic lugs | Hmi / hex / connect
37 | Cable glands | 3d / comet / hmi
38 | Lt cable jointing kits(cold curing) | Reychem/3m
39 | Pvc tape | Steel grip / isi apprved
40 | Pvc junction box | Hensel / clipsal / spelsberg / scame / sintex
41 | Ceiling fan / exhaust fan | Crompton / bajaj / orient / havells
42 | Electric timer | Siemens / legrand / l&t / meco /telemechanique
43 | Connectors (colours as per phase & neutral) | Wago / phoenix contact/ connectwell
44 | Industrial socket with mcb | Legrand / schneider/mennekes
45 | Modular switches, sockets & other accessories | Mk – blenze / legrand-arteor / schnedier-zencelo / norisys / l&t anchor - woods/ hpl - smart / c&s-primo / havells - crabtree
46 | Metal clad socket with mcb | Legrand / hensel / schneider / scame / spelsberg
47 | Public spaces light fixtures | Philips/ lighting technology/ regent/ zumtobel/ jaquar/ iguzzini/ erco / endo / bega / lumenpulse or
As per final approval of fixture by architects.
48 | Insulating mat | Jyoti / premier polyfilm limited (electromat)/
49 | Eathing material | Obo/jef/cape

## HVAC MAKE LIST
NAME OF PROJECT: Food Court at Eklera
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Thermal Insulation on Kitchen Duct | UP Twiga, Owens Corning, Supreme
9 | Air washer / Scrubber | Zeco/ Edgetech / Waves / Ambasdor / Airflow
10 | UPVC Drain Piping | Prince / Supreme
11 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
12 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
13 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
14 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
15 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
16 | Cables | Polycab / Finolex / Hawells
17 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
18 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
19 | ESP Filter | Honeywell/Magneto/Trion
20 | Split unit | Toshiba / Bluestar / Daikin / Samsung / Mitsubishi/LG/Hitachi /Voltas
21 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
22 | Inline Fans | AIRFLOW/HUMIDIN/ Carryair/ Kruger / System Air / Sphire Eq Approved
23 | Starter | Siemens / Allen Bradley/ ABB / Schneider / L & T
24 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
25 | Copper Pipes | Maxflow / Yorkshire / Rajco / Mehta tubes
26 | Copper Pipe fittings | Conex Banninger/ NIBCO
27 | Copper Pipe Insulation | Thermobreak / Supreme
28 | AHU Fan section | AIRFLOW/HUMIDIN/ Carryair/ Kruger / System Air / Sphire Eq Approved
29 | Air Handling Unit | Zeco/ Edgetech / Waves

## Domino's Material Specification (hidden)
Dominos - Standard schedule of Materials
SR.NO | Item | Material Code | Materials | Size in MM | Vendor /Code (OPT-01) | Vendor / Code (OPT -02) | Refer dwg no
A | Floor Tiles
1 | Floor Tiles | FF01 | Vitrified Tiles | 600 x 600 | Orient tiles- DGVT cemento grey 600 x 600 mm/Kajaria -Urbanity Cement | Somany -Ethos grey 600 x 600 mm | Flooring Plan -
2 | Floor Tiles | FF02 | Polished Vitrified Tiles | 600 x 600 | Orient tiles-Sahara crema 600 x600 mm/Kajaria-K6815 Slate | Somany -Matching with shade 600 x 600 mm | Flooring Plan -
3 | Floor Tiles | FF03 | Full bodied Vitrified Tiles | 300X1200(tread); 600X1200 (slab size) | Johnson Endura Stepping Stone -DONAPAULA PLAIN | Somany - Largo Stepon Verde 300 x 1200 & Largo Riser Verde 200 x 1200 | Flooring Plan -
4 | Floor Tiles | FF04 | Vitrified Tiles | 130X800 | Kajaria - Shesham Rosewood 130 x 800 mm | Somany - Strio Hector Wood Teak 196x1200 | Flooring Plan -
5 | Floor Tiles | FF05 | Vitrified Tiles | 130X800 | Kajaria -Shesham Nero 130 x 800 mm | Somany - Strio Salis Wood Wange 196x1200 | Flooring Plan -
B | Wall Tiles
1 | Brick Tiles | BK01 | Exterior Grade-Aggregate Material-German Handmade | 12mmX8"X2.5" | Articlad - ACG 795 | Unistone (Zara Red) / MCM(Code -A Series Brick 54058) | Booth Seating Area Wall
2 | Brick Tiles | BK02 | Exterior Grade-Aggregate Material-German Handmade | 12mmX8"X2.5" | Articlad -ACG 555 | MCM Clay Tile(Code -K series ,facing brick /052)/Unistone (White) | Storefront
3 | Wall tile | TL01 |  |  | Ceramic wall tile (Printed) With customize line work Make : -Johnson
4 | Wall Tile | TL02 |  |  | Ceramic wall tile white/ Satin white300x600mm (Plain) Make : -Johnson
C | Counter Cladding Tiles
1 | Tiles |  | Vitrified Tiles | 130X800 | Kajaria -Shesham Oak 130 x 800 mm | Somany - Strio Carrisa Wood Robble 196x1200 | Counter Fascia
2 | Tiles | FF05 | Vitrified Tiles | 130X800 | Kajaria -Shesham Nero 130 x 800 mm | Somany - Strio Salis Wood Wange 196x1200 | Counter & Floor
3 | Tiles |  | Vitrified Tiles | 130X800 | Kajaria - Mahogany 130 x 800 mm | Somany - Strio Rovver wood teak 196x1200 | Counter Fascia
4 | Tiles | FF04 | Vitrified Tiles | 130X800 | Shesham Rosewood 130 x 800 mm | Somany - Strio Hector Wood Teak 196x1200 | Counter & Floor
D | Toilet Tiles
1 | Floor Tile |  | Vetrified Tiles | 300X600 | Kajaria -Eternity -Amy Aazul | Somany -Matching with shade | Toilet Detail-
2 | Wall Tile |  | Vetrified Tiles | 300X600 | Kajaria-Eternity -Vogue Marfil | Somany -Matching with shade | Toilet Detail-
3 | Granite |  | Granite stone |  | Jet Black Granite |  | Toilet Detail-
E | Corian
1 | Corian Counter |  |  |  | LG ASPEN SNOW - AS 610 | SAMSUNG ASPEN GLOW -AG 636 | REHAU -FORST WHITE 180L
F | Fabric / Leather
1 | Leatherite | FB1 | Synthetic Leather |  | Bentley - 935 |  | Booth Seating
2 | Leatherite | FB2 | Synthetic Leather | 140 CM wide roll | Ddecor- Aura |  | Chair
G | Laminates / Veneer
1 | Laminate | LAM 01 | Laminate |  | 14554 RH Hooked Holz Acasia MERINOLAM |  | Generic Drawing
2 | Laminate | LAM 02 | Laminate |  | 21141 Snow White MERINOLAM |  | Generic Drawing
3 | Laminate | LAM 03 | Laminate |  | 21039 Misty Grey MERINOLAM |  | Booth Seating
4 | Laminate | LAM 04 | Laminate | - | -- | -- | --
H | Paint
| Paint shade | WF 01 | Lustre paint |  | Dark Shadow 8294 Asian Paints |  | Decoration Plan -
| Paint shade | WF 02 | Lustre paint |  | Rain Drop L143 Asian Paints |  | Decoration Plan -
| Texture | WF_03 | Lustre paint |  | Apex Duracast venezio (fine grain texture finish) | (Perlina Texture )
Sl. No. | Product Description | UOM | Qty. per Store | Approved Make | Approved Model No. | Approved Make | Qty per store
1 | 25x25x1500 mm ht. SS Brush finish square handle with lock | Nos. | 2 | Ozone | OGHC-S5(35X1500)SSS | Ozone | 2
2 | Top Pivot Fitting for Glass Door | Nos. | 2 | Ozone | OFS-ACC-TP | Ozone | 2
3 | Floor Spring | Nos. | 2 | Ozone | FS-9400 STD | Ozone | 2
4 | 100 mm wide Double Action SS Hinges | Nos. | 5 | Ozone | OZ-SSBH-SSS | Ozone | 5
5 | Door Closure | Nos. | RO | Dorma | TS 72 |  | RO
6 | Door Handle (22mm Ø x 300mm length) – Single Leaf Flush Door | Nos. | 1 | Dorma | ART No. TGDI30033S | Dorma | 1
7 | Door Lock (for flush doors other than Toilet) | Nos. | RO | Ozone | OZ-NL-22-STD SSS | Ozone | RO
8 | New Chrome Bathroom Vacant –Engaged Indicator Door Lock | Nos. | 1 | DOORCRAFT | SILVER LSTN-10 | Doorcraft | 1
9 | Tower Bolt | Nos. | RO | Ozone | OZ-B-SII | Ozone | RO
I | Adhesives
| Vamicol (Adhesive) | Make - Jivanjor (Multi-purpose Wood Adhesive for long lasting bonds)
| All Rounder (Synthetic Resin Adhesive) | Make - Jivanjor All Rounder is a ready to use premium quality white adhesive specially formulated to give unmatched bond strength, it is also enriched with special preservatives to prevent any bacterial growth during storage therefore providing it with a prolonged life.
| Termilok (Anti Termite wood Preservative) | (Prevents and kills Termites and Borers instantly,Penetrates deep into the wood Eco- Friendly and easy to apply product)
| Champion Super (Synthetic Rubber Adhesive) | Make - Jivanjor (Champion is a high performance synthetic rubber based adhesive with Solvent based Adhesive Fast curing & drying properties ,Delivers superior bond strength.)