## High Side CHW AHU
High Side CHW AHU BOQ
Sr. No. | Description | Unit | Qty | Rates | Amount
1.1 | Ceiling suspended Air Handling Unit - CHW Type
Supply of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per a. Chilled water temperature entering 7 deg C & exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side).
a | 5720 CFM, 9.0 TR | Nos. | 1 |  | 0
1.2 | Starter Panel
Supply of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW/HP).The starter shall comprise of all necessary power and control equipments including, Auto/manual selector switch, start/stop push button, LED indicators.
a | 4.14KW (6HP) | Nos. | 1 |  | 0
1.3 | Chilled Water pipe
Supply of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted as per specification and as requirements
a | 40 mm dia. | Rmt | 14 |  | 0
1.4 | Chilled Water pipe Insulation
Supply of insulation along with adhesive as per specifications and drawings.
a | 40 mm dia. | Rmt | 14 |  | 0
2 | CHW AHU Valve Station package
Supply of following valve station for air handling Unit. It shall include following Item: 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition
a | 40 mm dia. | Lot | 1 |  | 0
| Total |  |  |  | 0
| GST 28% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0

## Low Side CHW AHU
Low Side CHW AHU BOQ
Sr. No. | Description | Unit | Qty | Rates | Amount
1.1 | Ceiling suspended Air Handling Unit - CHW Type
Installation, testing and comissioning of double skin ceiling suspended air handling units complete with 25mm thick insulated panels, Forward curved DIDW Blower, cooling coil section with 6 Row CHW coil, filter section with filters, fan motor, drive set, mounting base damper etc.as per below: a. Chilled water temperature entering 7 deg C & exit 12 deg C b. Fan Outlet Velocity should not exceed 1800 FPM c. Coil face velocity should not exceed 500 FPM d. Filter velocity should not exceed 400 FPM (Access door and CHW pipe connection should be on RHS when viewed from filter side).
a | 5720 CFM, 9.0 TR | Nos. | 1 |  | 0
1.2 | Starter Panel
Installation, testing and comissioning of Direct online starters suitable for motors of Air handling units of below mentioned capacities (KW/HP).The starter shall comprise of all necessary power and control equipments including, Auto/manual selector switch.
i | 4.14KW (6HP) | Nos. | 1 |  | 0
1.3 | Chilled Water pipe
Installation, testing and comissioning of chilled water pipes in MS class C with necessary clamps, vibration isolator and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. Adequately supported on rigid supports duly painted.
a | 40 mm dia. | Rmt | 14 |  | 0
1.4 | Chilled Water pipe Insulation
Installation, testing and comissioning of insulation by applying adhesive as per specifications and drawings.
a | 40 mm dia. | Rmt | 14 |  | 0
2 | CHW AHU Valve Station
Installation, testing and comissioning of following valve station for Air Handling Unit . It shall include following Item: 1. Ball Valve for AHU drain - 1 nos. 2. Y-Strainer - 1 nos. 3. 2 way control valve - 1 nos. 4. Temperature gauge - 2 nos. 5. Pressure gauge - 2 nos. 6. Balancing valve-1 nos 7.Air release purge valve-1 nos 8.Butterfly valve-5 nos 9. Necessary Insulated copper Pipe - as per site condition
a | 40 mm dia. | Lot | 1 |  | 0
| Total |  |  |  | 0
| GST 18% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0

## Low Side BOQ
Low Side HVAC BOQ
Sr. No. | Description | Unit | Qty | Rates | Amount
1 | AIR DISTRIBUTION SYSTEM
1.1 | GI sheet metal rectangular duct
Supply, Fabrication, Installation, Testing & Commissioning of following gauges of ducting complete with splitters, neccessary supports, dampers, and turning vanes as per specification and HVAC layout. Aproved Makes: JINDAL, TATA, SAIL, Equivalent. All exposed ducts and supports shall be painting with 2 coats of primer & 2 coats of epoxy paint. (Make-JSW/ESSAR)
a | 24 gauge ducting - 0.63 mm thickness (Width upto - 750mm) | Sq. mt | 278 |  | 0
b | 22 gauge ducting - 0.80 mm thickness (Width 751 - 1500) | Sq. mt | 32 |  | 0
2 | Accoustic Insulation
| Accoustic lining of duct work with 25mm thick -32kg/m3 Density,Resin Bonded fibreglass Rigid Boards using shalikote primer hot bitumen and mechanically fastened Nuts & Washers,covered with RP tissue and 30 G aluminium perforated sheet as per specs. Makes : KIMMCO,OWEN'S CORNING, U P TWIGA. | Sq. mt | 30 |  | 0
3 | XLPE Insulation (Supply / Exhaust / Fresh Air Duct) :
Providing and fixing XLPE insulation by applying adhesive on ducts complete as per specifications and drawings. Make-SUPREME / PARAMOUNT. (Exhaust- out side insulation, Fresh air -outside insulation, Supply- Inside insulation, Supply-outside painted.)
a | 13 mm thick | Sq. mt | 305 |  | 0
4 | Thermal Exhaust Duct Insulation ( Only in BOH )
| Exhaust Air Duct insulation with 13mm thick heatlon insulation within store. No insulation for duct outside store. | Sq. mt |  |  | 0
5 | Thermal insulation- (Out side Building )
| Providing and fixing nitrial rubber by applying adhesive outside the ducts complete with 2 layer of UV paint and fiber glass cloth. (13mm thick) | Sq. mt |  |  | 0
4 | Continous / Linear Grilles
Extruded Aluminium Powder Coated Continous / Linear Grilles Of Required Airflow Angles (0/15/30/45 degree deflection: 1 or 2 way) with four side flanges as per requirements. (Make - AIRVISION/COSMOS)
a | 6" Width | Rmt | 7 |  | 0
b | 8" Width | Rmt | 7 |  | 0
5 | Supply Air Square Grille
Supply, installation of aluminium extruded white powder-coated supply air square grilles with four side flanges (0/22.5/45 degree deflection: 1 or 2 way), with aluminium powder coated, multiple flape type with dampers. (Kitchen Area)
a | Neck Size - 12" x 12" (Outer Size - 14" x 14") | Nos. | 8 |  | 0
6 | Return Air Square Grille
Return air square grills without damper shall be four side flanges with active sizes as given below.
a | Neck Size - 14" x 14" (Outer Size - 16" x 16") | Nos. | 11 |  | 0
7 | Canvass Connection
a | Installation of Double Canvass connection for all air outlet / inlet, Fire retardant type with GI flanges for Units. | Nos. | 7 |  | 0
8 | Volume Control Damper (make - Cosmos/ Caryaire/ Air Product)
| Supply & Installation of volume control damper made of 100x40x1.55mm thk galvanised steel frame & with opposed blades of 1.55mm galvanised sheet steel. | Sq. mt | 3 |  | 0
9 | Collar Damper (make - Cosmos/ Caryaire/ Air Product)
a | Supply & Installation of Collar Damper gear operated with vertical blades. | Sq.mt | 4 |  | 0
10 | Drain Piping
Supply, Installation, testing & commisioning of Drain Water piping work out of PVC / HDPE hard pipes with insulation Complete with T joints and bends
a | 32mm | Rmt | 6 |  | 0
11 | Air Curtain
a | 1200 mm Long | Nos. | 1 |  | 0
12 | Electrical Cabling
Providing and laying Electrical PVC CU armoured cable from Weather proof enclosure MCB to Cassette/ Hi-wall/ Ductable ODU or DOL starter to Air handling units with 12SWG Earth WIRE (with cable glands & lugs)
a | 3 C X 2.5 sq. mm. CU ARMOURED | Rmt |  |  | 0
b | 3 C X 4.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
c | 3 C X 6.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
d | 3 C X 10.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
e | 3 C X 16.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
f | 4 C X 2.5 sq. mm. CU ARMOURED | Rmt |  |  | 0
g | 4 C X 4.0 sq. mm. CU ARMOURED | Rmt | 20 |  | 0
h | 4 C X 6.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
i | 4 C X 10.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
j | 4 C X 16.0 sq. mm. CU ARMOURED | Rmt |  |  | 0
13 | Electrical work for HVAC
a | Supply and installation of all cabling, glanding, termination from starter panel to CSU. | Lot | 1 |  | 0
| TOTAL |  |  |  | 0
| GST 18% |  |  |  | 0
| TOTAL AMOUNT |  |  |  | 0

## Ventilation BOQ
VENTILATION BOQ Rates (per unit quantity)
Sr. No. | Sr. No. | Description | Unit | Qty | Rates | Amount
1 |  | VENTILATION UNIT FOR KITCHEN & TOILET
1.1 | 1 | AIR WASHER UNIT (with Fresh Air Filters)
|  | Supply of Cabinate type Air Washer Unit backward inclined DIDW blower with suitable high static pressure to create the required intake velocities and over come the pressure loss at the inlet of filters and ducts. DIDW Centrifugal blower. (Motor outside the effluent air stream.) Backward inclined, non over loading type. ( smaller motor) mounted directly on motor shaft. (slip losses and lesser maintenance) Dynamically balanced to provide a vibration free operation. Control Panel Wall mounted incorporated with suitable starter of make siemens/L&T with single phase prevention.Fan to be direct driven to motor. The unit shall have water pump for recirculating water, Filter and water elliminator. |  |  |  |  | Loft mounted Unit Front Suction & Back Discharge (Access door, pump, drain, makeup, overflow connection on LHS side from filter side.)
| a | 4100 CFM
|  | 4100 CFM (external Static Pressure: 100 mm) | Nos | 1 |  | 0 | Static pressure of the unit to be verified at site before execution as per the actual duct routing inside the store and existing duct provided by airport
1.1 | 2 | DRY SCRUBBER UNIT
|  | Supply,Installation, testing & commisioning of packaged type Exhaust Fan section along with Dry Type Scrubber, Stable placement of unit on respective foundation along with vibration isolation pad as per detail drawing / specification, connecting all wiring, cabling, ducting & other accessories as required to run unit acceptably.each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type even air flow distribution plate, stainless steel spiked ionizers to create high voltage DC field, honey comb patented cylindrical structure filter cell which should be alternatively charged positive and negative with large collecting area , to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity below shall be equipped with multiple protection functions for power and overload and overheating with interlock switch for safety as per approved specification and drawings). |  |  |  |  | Loft mounted Unit Front Suction & Back Discharge (Access door on LHS side from suction side.)
| a | 4500 CFM
|  | 4500 CFM (external Static Pressure: 100 mm) | Nos | 1 |  | 0 | Static pressure of the unit to be verified at site before execution as per the actual duct routing inside the store and existing duct provided by airport
| 3 | Freight ( Outstation) | Nos | 2 |  | 0
| 4 | Installation ( Outstation) | Nos | 2 |  | 0
|  | TOTAL |  |  |  | 0
|  | GST 18% |  |  |  | 0
|  | TOTAL AMOUNT |  |  |  | 0