## Low Side Work
ESTIMATED COST- HVAC
THIRD WAVE COFFEE , PARCEL C , HYDERABAD AIRPORT
HVAC WORKS
C | Part B: Low Side Works |  |  |  | 0
D | Part C: Electrical Works |  |  |  | 0
GRAND TOTAL
ESTIMATED COST- HVAC
THIRD WAVE COFFEE , PARCEL C , HYDERABAD AIRPORT
HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part C | Low Side Works
1 | Chilled Water Piping with Nitrile Rubber Insulation
Supplying, laying/ fixing, testing and commissioning of chilled water piping with Insulation with Class O nitrile Rubber pre-slit, pipe sleeve upto 100 mm dia and sheet for bigger dia with factory Laminated 7 mill woven glass cloth of thicknesses as specified, with approved adhesive. Manufactured supplied, suitable sized nitrile rubber pipe supports with PUF/PIR inserts shall be used. Thermal conductivity should not exceed 0.035 W/MK at 0 degree celsius and water vaper resisitance > 7000. Manufactures tapes and adhesive to used only. The pipe supports should also be of nitrile rubber with PUF/PIR inserts and are to be installed as per manufacturer's recomendation.
i | 40mm with 32mm thick | Mtrs. | 40 |  | 0
2 | Insulated Valves
2.1 | Manual Butterfly Valves
Providing and Fixing of the following valves with PN-16 Ratings complete with flanges /nuts/ bolts/gaskets etc. Butterfly valve shall have CI body seal of black nitrile rubber (tight shutoff) S.G. iron disc(nylon coated) PTFE coated shafts etc. as required. These valves should be suitable for flow in either direction and seal in both directions and should be integral moulded design.
2.1.1 | 40 mm dia -PN16 -- Insulation as per Chilled water pipe | Nos. | 2 |  | 0
2.2 | Dynamic Balancing Valve-PID type
Supply & installation, testing and commissioning of electronic self balancing valve with integrated two way modulating control valves in a single body. The actuator shall be capable of accepting 1-10 VCD 4-20A electrical signed and shall provided similar transcend feed back output singed to control system. The minimum close off pressure of actuator must be 1.5 times shut of head of pump as per Specification of following size.
2.2.1 | 40 mm dia- 9.0 TR AHU | Nos. | 1 |  | 0
2.3 | Stem Type Thermometer complete with thermowell etc.
2.3.1 | 6" long | Nos. | 2 |  | 0
2.4 | Dial Presure Guages with isolating valve & piping etc.
2.4.1 | 4" Dial | Nos. | 2 |  | 0
2.5 | Providing and Fixing of automatic air vent of approved make as per specifications/drawings
2.5.1 | 20mm dia | Nos. | 2 |  | 0
3 | DX SYSTEM
Providing and fixing copper piping with nitreal rubber with chaseling as per specifications and drawings.
a. | 5.5 TR Machine (Liquid Line + Gas Line) | Mtrs. | 50 |  | 0
(Note : 1RM is equal to 1 RM of gas line and 1 RM of liquid line)
4 | Drain Piping
Supply, erection, testing and commissioning of following sizes of 'B' Class G.I piping insulated with 9 mm thick Nitrile Rubber complete with G.I. fittings hangers supports,etc.as required.
4.1 | 32 mm dia | Mtrs. | 20 |  | 0
5 | DUCTING
5.1 | G.I. Sheet Metal Ducting - Factory Fabricated
Installation, Testing and Commissioning of factory fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
5.1.1 | 0.63 MM (24 Gauge) | Sqm. | 120 |  | 0
5.1.2 | 0.80 MM (22 Gauge) | Sqm. | 10 |  | 0
5.2 | G.I. Sheet Metal Ducting - Site Fabricated
Installation, Testing and Commissioning of site fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
5.2.1 | 0.63 MM (24 Gauge) | Sqm. | 10 |  | 0
5.2.2 | 0.80 MM (22 Gauge) | Sqm. | 10 |  | 0
6 | INSULATION
6.1 | Acoustic Lining
Supplying and fixing 13 mm thick closed cell elastomeric insulation of density 55 kg/cu.m.and K valueof not less than 0.037W/mk at 20 deg C as per specifications and drawings.
6.1.1 | 13 MM Thick | Sqm | 150 |  | 0
7 | DUCT ACCESSORIES
7.1 | Supply , Installation, Testing and Commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 2 |  | 0
7.2 | Supply , Installation, Testing and Commissioning of Al volume control grille damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | Sqm. | 2 |  | 0
7.3 | Supply ,Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Supply Air Grills as per specifications | Sqm. | 1 |  | 0
7.4 | Suppy , Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Supply Air diffusers with aluminium volume control dampers as per specifications | Sqm. | 1 |  | 0
7.5 | Supply ,Installation, Testing and Commissioning & fixing of powder coated extruded aluminium Return Air diffusers with aluminium volume control dampers as per specifications | Sqm. | 1 |  | 0
7.5.1 | 100 MM Aluminium Continuous Grille | RM | 15 |  | 0
7.5.2 | 150 MM Aluminium Continuous Grille | RM | 7 |  | 0
7.5.3 | 400 MM Aluminium Continuous Grille | RM | 10 |  | 0
Sub Total Part C |  |  |  |  | 0
Part D | Electrical Works
1 | Electrical Control Panel
Supply, installation, testing and commissioning of panel boards made of 2.0 mm thick steel sheet duly powder coated with voltmeter, ammeter, electronic energy meter, indicating lights, Stop/manual /Auto selector switch in each, outgoing current operated single phase preventer. The starters should have potential free contacts for connection to Building Automation System. The panel shall include contactors /over load relay with built in single phase protection / Time delay relay for delayed automatic start of the motor. All panels should have spare NO/ NC Contacts for BMS applications as required.
1.1 | Panel-P01
(1 x 1.5 KW)
OUTGOING
-- | 1 No. 16 Amps TP MCB - 3 Phase
-- | 1 No. DOL starter for 1.5 KW motor
-- | 1 No corresponding single phase preventer
-- | 1 No. Digital Type Ammeter
-- | Each star-delta/DOL starter consists of current operated MN type over load relay, contactor, push button, ON/OFF indication light | Set | 1 |  | 0
2 | Isolators
2.1 | 16 Amps TPN Isolator | Nos. | 1 |  | 0
3 | Cables
Supplying, laying, testing and commissioning of XLPE insulated copper conductor armored cables of 1.1 KV grade of following sizes directly on wall/structural frame/ cable trays or racks using approved type of clamps,End terminations with Double Compression type glands on both ends, double earthing with GI strip/wire of suitable size and hardware as per specifications.
3.1 | 3 C x 4 Sq. mm | Mtrs | 25 |  | 0
3.2 | Control & Transmission Wiring
3.2.1 | Providing & fixing control cum transmission wiring of 2 core x 1.5 sqmm copper in MS conduits between indoor and out door unit and between indoor units and their remote sensor/controller. | RM | 30 |  | 0
3.3 | Power Cabling
3.3.1 | Indoor Units
3.3.1.1 | Providing and fixing flexible power cable of 3 core x 1.5 sqmm copper between Indoor units and their power points | RM | 10 |  | 0
4 | Earthing
| Supplying and laying of the following earthing clamped to wall with suitable clamps saddles and fixing bolts/ in ground including the cost of digging and back filling as required and complete as required to comply with IS 3043:1987. All copper joints shall be tinned. The rates shall be inclusive of making test joints where ever required | Lot | 1 |  | 0
4.1 | 25 mm x 3 mm GI strip | RM | 10 |  | 0
4.2 | 8 SWG GI Wire | RM | 10 |  | 0
Sub Total Part D |  |  |  |  | 0