## HIgh Side Work
ESTIMATED COST- HVAC
THIRD WAVE COFFEE , PARCEL C , HYDERABAD AIRPORT
HVAC WORKS
A | Part A: HVAC Equipments |  |  |  | 0
B | Part B: DX Equipments |  |  |  | 0
ESTIMATED COST- HVAC
THIRD WAVE COFFEE , PARCEL C , HYDERABAD AIRPORT
HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part A | HVAC Equipments
1 | Air Handling Units (Indoor Type)
Supply ,Installation , Testing & Commissioning Of Double skin Ceiling Suspended Type air handling units of extruded aluminium section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside, minimum of 25 mm thick PUF insulation of 40KG/m3 , Backward/ Forward Curve DIDW centrifugal Blowers with TEFC motors, minimum 6 Row Deep copper cooling coils, with aluminium fins, MERV 8 Filters. The drain pan shall be constructed out of 18G stainless steel duly insulated. All the AHU's installed under this tender shall have IE3 motor. All the cooling coils shall be AHRI / Eurovent Certified . The AHU Coil shall be selected at 9 deg C Chilled water Inlet Temp and 14 deg C Chilled Water Outlet Temperature and flow rate of 2.4 USGPM/TR. Approval of AHU Technical Data by consultant prior to fabrication is required.
1.1 | Air Handling Units
1.1.1 | 6800 CMH(4000 CFM), 6 RD, 20 mm External SP , 1.5 KW Motor , 9.0 TR With Backward Curved Blowers | Nos | 1 |  | 0
Note :
1. Cost of fire retardant canvas connections shall be included in the unit price .
Sub Total Part A |  |  |  |  | 0
Part B | DX EQUIPMENTS
1 | Air Cooled Split units (Min. 3 Star Rated, R-410 Refrigerant)
Supply Installation, Testing and Commissioning of Air Cooled Split airconditioners each comprising an outdoor unit consisting of hermetic rotary / scroll compressor, air cooled condensing unit, Condenser fan etc. with outer casing and indoor fan coil unit(s) consisting of centrifugal fans, fan motor, DX cooling coil, outer casing, filter, control and power panel with remote control etc.
a) | Ductable Units
1.1 | 5.5 TR Unit with single ref.circuit | Nos. | 1 |  | 0
| Sub-Total Part-'B' Rs. |  |  |  | 0