## Electrical Works
Project Name : Chai Point MIAL T1
Electrical Works
Sl No | ITEM DESCRIPTION | UNIT | QTY
Total
1 | LT SWITCHGEAR and Distribution Boards
Supply, installation, testing and commissioning of Low voltage switchgear's, free standing, Cubical type, dead front, Frame and Doors:2mm, Internal Partations:1.6mm thick, Gland Plates:3mm Thick, powder coated (Paint Shade: RAL 7032/7035), indoor type with vermin proof hinged lockable doors for each compartment, bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications comprising of ACB,MCCB and MCB horizontal and vertical aluminum bus bar, earth bus bar as per SLD. All meters shall be digital with LED display, whereever mentioned and shall have RS 485 Modbus RTU half duplex communication interface for provision of BMS connectivity and wired accordingly. Provide required NO/NC potential free contacts wires and terminal blocks in the cable alley for BMS operation (Optional).The swtichboards are to be tested as per IS 8623 -1977 specifications. The busbars are of high conductivity Al. alloy E91E IS 5082 specification and cable entries will be from either top or bottom depending on location. LT Switchgear shall be as per technical specification and single line diagram
1.1 | MDB
| MDB shall be as per Single line diagram and technical specifications.(Indoor -IP 42) | Nos | 1
1.2 | ISOLATORS
a | 160A 4P MCCB in metallic enclosure -IP 42 | Nos | 1
e | 40A DP MCB in metallic enclosure -IP 42 | Nos | 2
Total - Section-1
2 | MCB Distribution boards
a | 12 Way TPN MCB Distribution Board -PPI (KDB) | Nos | 1
MCB DB comprising the following
Type of DB - 12 way TPN PPI MCB DB (Double Door)
100A 4P MCB - 1 No. as incomer
63A DP RCCB, 30mA, 2 Module - 3 Nos. as Sub incomer per phase
20A SP MCB, 10 kA - 29 Nos. as outgoings : MCB are of 'C' Curve
32A SP MCB, 10 kA - 1 Nos. as outgoings : MCB are of 'C' Curve
The rate shall include providing Cu. bus barsinterconnection, separate earth bus, separate neutral bus for each phases, Blank Plates and incluuding necessary connected civil works like chipping, rough plastering etc.
3 | LOW VOLTAGE CABLES AND END TERMINATION
3.1 | Low voltage Aluminium conductor cables
Supply and laying of 1100 V grade, XLPE insulated,extruded PVC Inner Sheathed and extruded FRLS-PVC Outer sheatehed , aluminium conductor, Armoured power cable as per specifications. The cable shall be laid in indoor trenches / cable trays as required. The cable shall be clamped at regular intervals to the suppoprts in trench or to cable trays or brick wall using MS clamps and fasteners. Rate shall exclude the cost of cable trays and termination in this item.
NOTE: Cables will not be procured based on BOQ only. True measurements will be taken by Contractor before ordering, based on Drawings/ Site actual requirements ( Applicable to all respect Line items)
a | 3.5CX 50Sqmm Alu.arm Cable | Rmt | 30
e | 4CX 10Sqmm Alu.arm Cable | Rmt | 15
3.2 | Low Voltage Copper Conductor Cables
Supply and laying of 1100 V grade, XLPE insulated,extruded PVC Inner Sheathed and extruded FRLS-PVC Outer sheatehed copper conductor, Armoured/Un armoured power cable as per specifications. The cable shall be laid in indoor trenches / cable trays as required. The cable shall be clamped at regular intervals to the suppoprts in trench or to cable trays or brick wall using MS clamps and fasteners. Rate shall exclude the cost of cable trays and termination in this item.
Armoured Copper Cables :
a | 4Cx 16sqmm Cu Arm Cable | Rmt | 15
b | 4Cx 6sqmm Cu Arm Cable | Rmt | 15
c | 4Cx 4sqmm Cu Arm Cable | Rmt | 20
e | 3Cx 4sqmm Cu Arm. Cable | Rmt | 20
3.3 | Copper Flexible Cables :
a | 3Cx6sqmm Cu Flexible Cable | Rmt | 20
3.5 | Armoured Copper Cables :
a | 4Cx 16sqmm Cu Arm Cable | Nos | 2
b | 4Cx 6sqmm Cu Arm Cable | Nos | 2
c | 4Cx 4sqmm Cu Arm Cable | Nos | 2
e | 3Cx 4sqmm Cu Arm. Cable | Nos | 2
3.6 | Copper Flexible Cables :
a | 3Cx6sqmm Cu Flexible Cable | Nos | 8
Total - Part 3
4 | SWITCHES AND SOCKETS
Supply and install switches and Sockets System as required according to the specification, drawings and design. The installation rate of all the following accessories shall include for the supply of all materials such as passivated metal switchbox,junction boxes, switch plate, switches, conduit accessories, wires, tags, supports, fittings fixings and the like, to form complete elements and shall include for earthing the switchboxes The installation rate shall include for termination of all cables and wires into the devices, testing,commissioning and setting to work as required by the specifications.
NOTE: SWITCHES AND SOCKETS will not be procured based on BOQ only. True measurements will be taken by Contractor before ordering, based on Drawings/ Site actual requirements ( Applicable to all respect Line items)
Power Receptacles with Box
4.2 | Supply, installation, testing and Commissioning of 1 x 6A, universal socket controlled with 1 x 6A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | 10
4.3 | Supply, installation, testing and Commissioning of 2 x 6/16A,, universal socket controlled with 2 x 16A Switch including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish | Nos | 5
4.6 | Supply, installation, testing and Commissioning of 1 x 20A, universal socket controlled with 1 x 20A Switch floor mounted pop up box including interconnection etc., complete.The sockets shall be with face plate, GI BOX with accessories.Rate shall include the cost for fixing of back box with plastering and rough finish (MK Type Floor Box) | Nos | 15
Power Receptacles without Box
4.7 | Supply, Installation testing and commissioning of 3 nos. of 6/16 A, multi Pin Universal socket controlled by 1 no. 16 A common switch along with face plate, raceway/Table mounted and other necessary accessories to complete the installation. | Nos | 2
Industrial Sockets :
4.9 | Supply, installation, testing and Commissioning of 20A, 1 phase Industrial Plug & Socket controlled with 20A DP MCB in a enclosure with all accessories. (IP65) | Nos | 15
4.16 | Supply and fixing of Blankplates | Nos | 2
4.17 | Supply and fixing of 3 Pin Plug top suitable for 16/20A | Nos | 2
Total - Section - 4
5 | CIRCUIT MAINS
CIRCUIT MAIN FOR LIGHTING/POWER :
Supply and drawing of 1100V grade, multi strand FRLS insulated copper conductor wire. drawn into existing raceways/cable trays with necessary fixing accessories.
5.1 | 3 core 1.5 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/Conduit in this items. | Rmtrs | 35
5.2 | 3 core 2.5 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 50
5.3 | 3 core 4 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduit. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 50
5.7 | 1 core 4 sqmm Double Insulated Copper copper conductor flexible cable with FRLS Sheathing in the existing raceways/conduits. Rate shall exclude the cost of Raceway/conduit in this items. | Rmtrs | 70
Total - Section - 5
6 | POINT WIRING
Point wiring of light, using 1100 volt grade, 3Rx1.5Sqmm multi strand FRLS insulated copper conductor flexible cable, drawn in existing raceways/Conduit. The rate shall include providing mounting boxes with tapped holes for lights switches, moulded front plates with brass screws earthing of all points using third core of the cable, For MCB Controlled Lights -DB to 1st light will be measured as circuit wiring.The point wiring shall be as per specification.Rate shall exclude the cost of MCB,Rceways in this item.(CONDUIT - GI)
6.1 | PRIMARY LIGHT POINT (Switch Control)
| Primary light point means wiring from first switch control to the first light outlet. The switch and all necessary accessories would be part of primary point.'. Not to include the incoming lighting circuit from MCB-DB to switch.' But to include the sub-circuit if it is drawn from adjacent switch box. Ceiling flexible conduit shall be included at the drop of light fixture. | Nos | 10
6.2 | SECONDARY LIGHT POINT (Switch Control)
| Secondary light point means extention of light outlet from existing primary point. Same to be controlled by the existing switch of primary point. Ceiling flexible conduit shall be included at the drop of light fixture. | Nos | 25
Total - Section - 6
7 | CABLE TRAY/RACEWAYS
7.2 | Perforated Type
Supply and providing MS Perforated cable trays factory fabricated out of 2mm thick pre galvanized sheet steel, channel size 50 mm supporting angle frame at every 1.8 m, bottom angle fasteners, anchor grip bolts, synthetic enamelled painting, etc. The tray shall be suspended from ceiling using anchor bolt and angle iron supports or mounted from wall. The rate shall include all accessories like bends, elbows, tees, coupler plates, etc., which will be measured as linear measurement and fixing accessories.The rate shall include the cost of Supports
a) | 50 mm wide 50 mm height | Rmtrs | 12
7.7 | POWDER COATED FRAME FOR MCB DB's
a | Supply and Installation of DB Frame with wire ways shall be made out of 1.6mm thick CRCA sheet steel and powder coating colour shall match the colour of MCB DB's with hinged type door. 100mm x 100mm 1.6mm thick, wire ways / Raceway with 2mm thick screwed / press to fit cover with hinged type door for making Frame for MCB DB's. Complete required including installation accessories. | Rmtrs | 5
Total - Section - 7
8 | EARTHING
8.3 | Supply and running of below listed sizes of electrolytic copper / GI earth conductor tapes / wires and laid along with cable or clamped to brick wall, etc., as required.
a | 8 SWG GI wire for Earthing | Rmtrs | 40
b | 25x3mm GI Flat | Rmtrs | 25
d | 1Cx6sqmm Cu Flexible Cable Earthing (Green) | Rmtrs | 75
e | 1Cx4sqmm Cu Flexible Cable Earthing (Green) | Rmtrs | 50
Total - Part 8
9 | PVC pipes (Electrical/IT/AV/CCTV/ACS)
GI pipes (Electrical/IT/AV/CCTV/ACS)
9.2 | Supply and laying of 2 mm thick rigid MS conduits in concealed/Open conduit system using conduit accessories like junction boxes, collars, bends, elbows, binding wires, etc.
a | 32 mm dia conduit | Rmtrs | 10
b | 25 mm dia conduit | Rmtrs | 50
c | 20 mm dia conduit | Rmtrs | 10
Total - Section - 9
11.7 | Temporary Works
c | Preparation and Submission of as built drawings of total work executed (2 Sets hard and soft copy) | Nos | 1
Total - Section - 11
12 | LIGHT FIXTURES
12.1 | TRACK MOUNTED LED SPOT LIGHT MADE OF ALUMINIUM DIA CAST COMPLETE upto 20watts LAMP WT LED | Nos | 12
12.2 | LED SURFACE MOUNTE DOWN LIGHTER MADE OF ALUMINIUM DIA CAST COMPLETE WITH EDISION LED AND DRIVAR LAMP up to 22 WT LED | Nos | 5
Total - Section - 12
13 | UPS
a | Supply, Installation, Testing & Comissioning of: 5 KVA 1 Phase input/1 phase output UPS with 90 mins. Backup Battery Type: SMF with racks & enclouser (Output Power Factor Unity ) | Nos | 1
Total - Section - 13