## HVAC
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | DILLI STREAT_DELHI AIRPORT |  |  | DATE: | 2024-01-09
|  |  |  | REV: | R0
HVAC SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
HVAC EQUIPMENTS ( CHILLED WATER TYPE )
A.1 | Supply, Installation, Testing, and Commissioning of Chilled water type Single Skin Ceiling Suspended Air Handling Unit (AHU) of approved make with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment.
A.1.1 | 5.0 TR - (2000 CFM) | Nos | 1
A.1.2 | 7.5 TR - (3000 CFM) | Nos | 2
KITCHEN EQUIPMENTS
A.2 | Supply, installation, testing, commissioning and field performance of ceiling suspended Kitchen Exhaust Fan with all necessary supports and fittings.
A.2.1 | 5250 CFM | Nos | 1
A.2.2 | 3450 CFM | Nos | 1
A.2.3 | 5000 CFM | Nos | 1
A.3 | Supply, installation, testing, commissioning and field performance of ceiling suspended Electrostatic Precipitator (for removal of Kitchen Grease and Smoke particles) with all necessary supports and fittings. (Make: Rydair, Trion or equivalent with airport approval).
A.3.1 | 5250 CFM | Nos | 1
A.3.2 | 3450 CFM | Nos | 1
A.3.3 | 5000 CFM | Nos | 1
A.4 | Supply, installation, testing, commissioning and field performance of ceiling suspended Air Washer Unit with all necessary supports and fittings.
A.4.1 | 4200 CFM | Nos | 1
A.4.2 | 2760 CFM | Nos | 1
A.4.3 | 4000 CFM | Nos | 1
B | AC PIPING
HVAC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make: Astral, Supreme or equivalent with airport approval).
B.1.1 | 25 mm Ø | Mtr | 20
B.1.1 | 32 mm Ø | Mtr | 25
HVAC WATER PIPING
B.2 | Supply, installation and testing of MS class (C) Pre-Insulated Chilled Water Pipe with Poly urethane foam (PUF) insulation of minimum 36 kg/cu.m density and AL jacket or cladding with all necessary fittings, connections, flanges and all necessary pipe supports, clamps as applicable and as per site conditions. (Make: Jindal (Hissar), Tata Steel, SAIL or equivalent with airport approval).
B.2. | 40 mm Ø (Insulation thickness - 32 mm) | Mtr | 36
B.2.2 | 32 mm Ø (Insulation thickness - 32 mm) | Mtr | 26
C | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
C.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.1.1 | 22 Gauge - (0.85 mm Thick) - Supply Air Duct | Sq.Mtr | 45
C.1.2 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 23
C.1.3 | 22 Gauge - (0.85 mm Thick) - Make-Up Air Duct | Sq.Mtr | 45
C.1.4 | 24 Gauge - (0.70 mm Thick) - Make-Up Air Duct | Sq.Mtr | 40
C.1.5 | 22 Gauge - (0.85 mm Thick) - Return Air Duct | Sq.Mtr | 20
C.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
C.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 65
ROUND DUCTS
C.3 | Supply, installation, and testing of Galvanized Iron (GI)/ Galvanized Steel (GS) factory fabricated Spiral Round Ducts with all necessary fittings, round connectors, duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction.
C.3.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 22
FLEXIBLE DUCTS
C.4 | Supply, installation, and testing of aluminium-polyester casig Round Flexible Duct reinforced with spiral wound steel wire, Temperature range -20° C to +140° C, with a standard insulation thickness of 25 mm and with all necessary connections, fixing and support arrangements of approved make.
C.4.1 | 300 mm Ø | Mtr | 35
C.5 | Supply, installation, and testing of Flexible Duct Connectors to isolate vibrations and noises caused by air handling units , fans or any other equipments connected to the duct with air tight fittings with all necessary accessories.
C.5.1 | For AHU | Nos | 3
D | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
D.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.1.1 | 19 mm thicknesses - (SAD) - External Duct Insulation | Sq.Mtr | 72
D.1.2 | 19 mm thicknesses - (MUAD) - External Duct Insulation | Sq.Mtr | 85
D.13 | 19 mm thicknesses - (RAD) - External Duct Insulation | Sq.Mtr | 20
D.2 | Supply, installation & testing of Thermal Insulation of ducting using Aluminium foil faced resin bonded fibre Glass wool of density not less than 48 kg/m3. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.2.1 | 80 mm thicknesses - (KED) - External Duct Insulation | Sq.Mtr | 65
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
D.3 | Supply, installation & testing of Acoustic Insulation of ducts using opencell processed elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.045 W/(m-K) at 0° C and Fire performance according to building regulations - Class 1 as per BS 476, with very good sound absorption, damping and barrier properties. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
D.3.1 | 15 mm thicknesses - (SAD) - Internal Duct Lining | Sq.Mtr | 18
E | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
E.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Opposed Blade Damper / Collar Damper with Nylon gears and lever on face side for smooth operation. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
E.1.1 | Size - 500 x 500 mm | Nos | 7
E.1.2 | Size - 500 x 250 mm | Nos | 1
E.1.3 | Size - 300 x 250 mm | Nos | 10
E.1.4 | Size - 300 x 200 mm | Nos | 1
E.1.5 | Size - 250 x 250 mm | Nos | 9
E.1.6 | Size - 250 x 200 mm | Nos | 1
F | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
F.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Square Grille with fixed Aerofoil Blades, with 30° deflection - 1 Way with rigid frame of 16mm flange as standard. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.1.1 | Neck Size - 500 x 500 mm | Nos | 7
F.1.2 | Neck Size - 200 x 200 mm | Nos | 1
F.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Rectangular Grille with fixed Aerofoil Blades, with 30° deflection - 1 Way with rigid frame of 16mm flange as standard. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 900 x 400 mm | Nos | 2
F.2.2 | Neck Size - 800 x 400 mm | Nos | 1
CEILING DIFFUSERS
F.2 | Supply, installation, tetsing and commissioning of Aluminium Round Diffuser with circular cones for throw in circular patern and inbuild butter fly damper, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
F.2.1 | Neck Size - 350 mm Ø | Nos | 21
G | TESTING & COMMISIONING
G.1 | Air Balancing & Chilled Water Testing & Commisioning | Lot | 1
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## ELEC
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | DIAL_T1_DILLI STREAT |  |  | DATE: | 2024-01-09
|  |  |  | REV: | R0
ELECTRICAL SERVICES, CCTV & DATA - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
Item Code | Item Name | UOM | Qty | UNIT COST | REMARKS
A | INCOMER ISOLATOR / MCCB PANEL
A.1 | Supply, Installation, Testing & Commissioning of Incomer Isolator / MCCC Panel complete with Enclosure (If required as per site condition / Airport TDM). Make : Electrical Panel / DB's & Creakers (MCC, RCBO, ELCB & MCBC) : Legrand, ACC, Schneider, Siemens or equivalent.
A1.1 | 160A ISOLATOR / MCCB PANEL | Nos. | 2
A1.1 | 125A ISOLATOR / MCCB PANEL | Nos. | 1
B | METER / METER PANEL
B.1 | Supply, Installation, Testing & Commissioning of kWH / MFM Energy Meter Panel complete with Enclosure (If required as per site condition / Airport TDM). Make : Schneider, Secure, L & T or equivalent with Airport approval.
B.1.1 | 160A/5A ENERGY METER (CT TYPE) | Nos. | 2
B.1.2 | 125A/5A ENERGY METER ( DIRECT TYPE) | Nos. | 1
C | LV CABLING
C.1 | Supply, Installation, Testing & Commissioning of Fire Rated LS/LSZH PVC insulated PVC sheathed, Copper conductor, Steel Tape / Wire Armoured, 1100V grade cable, Number of Cable Core as per SLD / Load Calculation Sheet (Main Cable) & Unarmoured Single Core Wire (ECC), complete with Termination of the same with Single Compression Crass Glands, Solderless Tinned Copper Lugs, Gland earthing, etc. The cable shall be laid Underground / on Cable Tray / through Cable Trunking / in Pipe / on Wall / Trench as required. Make : Electrical Wires & Cables: Polycab, KEI, RR, Havells, Gemco or equivalent. For cables laid on Cable Tray / in Pipe / on Wall / Trench - the rate shall include necessary supporting / clamping arrangements.
C.1.1 | 1C x 50 MM2 Wire | Mtr. | 24
C.1.2 | 1C x 35 MM2 Wire | Mtr. | 12
C.1.3 | 1C x 25 MM2 Wire | Mtr. | 6
C.1.4 | 1C x 16 MM2 Wire | Mtr. | 3
D | DISTRICUTION BOARDS
D.1 | Supply, Installation, Testing & Commissioning of Surface / Flush mounting 10kA / 25kA (As per Panel requirement) Distribution boards. The DB shall be made out of 1.2 mm CRCA sheet steel enclosure and powder coated complete with cable gland plate & knock out at the top and bottom. The DB shall have hinged lockable door. The busbar shall be tinned copper, for phases mounted on suitable type Insulator, Independent neutral busbar including interconnecting wiring & earth bus on insulation mount. Make : Electrical Panel / DB's & Creakers (MCC, RCBO, ELCB& MCCB) : Legrand, ACC, Schneider, Siemens or equivalent. All DB's must named as per the SLD / Load Calculation Sheet. Laminated SLD & Load Calculation Sheet shall be placed near to DB Panel Locations. The RCCB / RCBO shall Ce Hpi / Si series & MCB's shall Ce 'C" / 'B' Curve (As per requirement).
SMDB
D.1.1 | 12 Way TPN Panel Board with 125A 30mA 4P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
EQP SMDB
D.1.2 | 8 Way TPN Panel Board with 160A 30mA 4P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
LPDB
D.1.3 | 18 Way TPN Panel Board with 160A 30mA 4P RCBO incomer,and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
UPS DB
D.1.4 | 6 Way SPN Panel Board with 20A 30 mA 2P RCBO incomer and outgoings as per SLD & Load Calculation Sheet. | Nos. | 1
E | LIGHT FIXTURES POINT WIRING
E.1 | Supply, Installation, Testing & Commissioning of Light Fixture Point wiring (Light Fixtures to be as approved by Architect Design & BOQ) with Lamps, Callasts / Drivers / Starters, Switches / Lighting Control Switch Board with Fire Rated LS/LSZH PVC insulated FlexiBle Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI Cack boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Light Fixtures : Philips, Wipro, Havells or equivalent. Make : AKG, CEC (ISI marker) or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
E.1.1 | TRACK LIGHT (Point Wiring only) | Nos. | 47
E.1.2 | DOWN LIGHT-01 (Point Wiring only) | Nos. | 64
E.1.3 | DOWN LIGHT-02 (Point Wiring only) | Nos. | 36
E.1.4 | PENDANT LIGHT-01 (Point Wiring only) | Nos. | 4
E.1.5 | PENDANT LIGHT-02 (Point Wiring only) | Nos. | 4
E.1.6 | PENDANT LIGHT-03 (Point Wiring only) | Nos. | 7
E.1.7 | BIRD SHAPE PENDANT LIGHT-01 (Point Wiring only) | Nos. | 11
E.1.8 | BIRD SHAPE PENDANT LIGHT-02 (Point Wiring only) | Nos. | 12
E.1.9 | BIRD SHAPE PENDANT LIGHT-03 (Point Wiring only) | Nos. | 11
E.1.10 | 600x600mm LED PANEL LIGHT (Point Wiring only) | Nos. | 19
E.1.11 | SQUARE LED PANEL LIGHT (Point Wiring only) | Nos. | 3
E.1.12 | ROUND LED PANEL LIGHT (Point Wiring only) | Nos. | 18
E.1.13 | LED STRIP LIGHT WITH DIFFUSER (12.77 Mtrs)(Point Wiring only) | Nos. | 1
E.1.14 | SIGNAGE LIGHTS (Point Wiring only) | Nos. | 6
E.1.15 | SUSPENDED SIGNAGE LIGHTS (Point Wiring only) | Nos. | 1
E.1.16 | LIGHTING CONTROL SWITCH COARD WITH SWITCHES AS REQUIRED (Point Wiring only) | Nos. | 6
E.1.17 | EXIT LIGHT (Wall / Ceiling Mounted) | Nos. | 5
F | WIRING DEVICES (SWITCHES & SOCKETS)
F.1 | Supply, Installation, Testing & Commissioning of Wiring Devices (Switches & Sockets - Face Plate Finish as approved By Architect / Matching to Architecture Finishes) with Fire Rated LS/LSZH PVC insulated Flexible Copper Wires 660/1100V grade through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI back Boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with Solderless Tinned Copper Lugs, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Wiring shall be as per IS 732. Make : Switch & Sockets : Anchor Roma / Penta, Legrand, Havells CraCtree, Finolex, L & T Switchgear or equivalent with Airport approval. Make : PVC Conduits : AKG, CEC (ISI marker) or equivalent. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / Crackets for conduit and Trunking suspension.
F.1.1 | 13A SINGLE SWITCHED SOCKET OUTLET | Nos. | 47
F.1.2 | 13A DUAL SWITCHED SOCKET OUTLET | Nos. | 3
F.1.3 | 16A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 18
F.1.4 | 20A SINGLE PHASE INDUSTRIAL SWITCHED SOCKET (3 PIN) (WALL MOUNTED) | Nos. | 18
F.1.5 | 63A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 2
F.1.6 | 32A THREE PHASE INDUSTRIAL SWITCHED SOCKET (5 PIN) (WALL MOUNTED) | Nos. | 8
F.1.7 | 20A UNSWITCHED FUSED CONNECTION OUTLET WITH-OUT NEON INDICATOR | Nos. | 1
F.1.8 | 20A DOUCLE POLE SWITCH WITH NEON INDICATOR | Nos. | 1
F.1.9 | 16A SINGLE PHASE ISOLATOR | Nos. | 3
F.1.10 | 20A THREE PHASE ISOLATOR | Nos. | 6
G | CONTAINMENT (CABLE TRAY & TRUNKING)
G.1 | Supply & Installation of GI Cable Tray & GI Cable Trunking, through Wall / Ceiling / Floor as per drawings, complete with standard accessories / factory made fittings, earthing throughout the run with copper braids, wall / ceiling suspended supports, etc. Make : Cable Management System : MEM, Profab (ISI marked) or equivalent.
G.1.1 | 50 x 50 MM CABLE TRUNKING | Mtr. | 78
H | UPS SYSTEM
H.1 | Supply, Installation, Testing & Commissioning of UPS along with required Cattery for specified back-up time, complete with battery Stand (If required) & standard accessories / equipments required for complete functioning of the system, earthing, support system (if required), etc. Make : UPS System : Luminous, APC, Microtek or equivalent with Airport approval.
H.1.1 | 4 KVA Single phase UPS with 30 Minute Cack-up | Nos. | 1
I | CCTV SYSTEM
I.1 | Supply, Installation, Testing & Commissioning of CCTV System with suitable / required cabling through suitable size GI Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with CCTV console / DVR, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : CCTV System : Hikvision, Honeywell, Dahua, or equivalent with Airport approval. Make : GI Conduits : Techno Flex India, K. M. Cables & Conduits or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
I.1.1 | CCTV Dome Camera, 4 Megapixel / As approved or confirmed Cy client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. (Ceiling mount) | Nos. | 11
I.1.2 | CCTV Dome Camera, 4 Megapixel / As approved or confirmed Cy client, Real Day / Night, Exir, IR LED, IP 67, with all neccessary accessories, Power supply units etc. (wall mount) | Nos. | 1
I.1.3 | DVR with 45 Days Back-up | Nos. | 1
J | DATA NETWORK SYSTEM
J.1 | Supply, Installation, Testing & Commissioning of Data & Telephone Network System with required cabling through suitable size GI Conduit / Heavy Duty PVC Conduit / GI Trunking (Containment size & Type selection as per site requirement), complete with suitable GI back boxes, Earthing, accessories, flexible conduits, glands, saddles, supports, ropes for future wire pulling, Labeling of wires etc. with Termination of the same with IDF Rack, etc. carrying out Surface / Concealed wiring as per site condition & maintain aesthetic of the unit. Make : IT Cables & Accessories : Belden or equivalent with Airport approval. The rate shall include wall chasing, chipping of floors, rough plastering, providing suitable supports / brackets for conduit and Trunking suspension.
J.1.1 | Dual Data outlet (RJ45) Jack | Nos. | 7
J.1.2 | Single Data outlet (RJ45) | Nos. | 14
J.1.3 | Patch Cords (1.5 meters length) | Nos. | 28
GRAND TOTAL NET
NOTE : The quantities mentioned in the above BOQ includes services only inside the site location (Building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## PHE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | DILLI STREAT |  |  | DATE: | 2024-01-09
|  |  |  | REV: | R0
PLUMBING SYSTEM - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | DRAINAGE SYSTEM
INTERCEPTORS & SEPERATORS
A.1 | Supplying, Installing, Testing & Commissioning of Greese Trap or Grease Interceptor (Above Ground / floor) of 304 grade stainless steel material with interceptor body, preforated bucket, baffles, integral trap, inlet & outlep pipe sleeve and stainless steel interceptor cover of approved make and with all necessary fittings & connectors etc. (Make : Nugreen , Kessel and Concessionaire can propose another make in SS material.)
A.1.1 | NGT 8 - Flow Rate (0.30 LPS / 18 LPM) | Nos | 2
A.1.2 | NGT 14 - Flow Rate (0.46 LPS / 28 LPM) | Nos | 3
A.1.3 | NGT 70 - Flow Rate (2.20 LPS / 132 LPM) | Nos | 1
VALVES & ACCESSORIES
A.2 | Supplying, Installing, Testing & Commissioning of ABS Air Admittance Valve conforming to EN 12380, with an air admittance air flow rate of 6.1 L/s and a temperature range of operation from -20 C to + 60 C of approved make with all necessary adapters, fittings and connectors etc. (Make : Astral/Supreme for Pipe and Fittings)
A.2.1 | 32 mm Dia | Nos | 9
DRAINS, TRAPS & CLEANOUTS
A.3 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 300 X 300 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
A.3.1 | 75 mm Dia - Outlet | Nos | 9
A.3 | Supplying, Installing, and testing of AISI 304 grade Stainless Steel Floor Drain with top square anti-slip mesh grating drain cover of 600 X 300 mm, lateral/horizontal outlet, with removable waste basket, odor water seal trap of approved make with all necessary adapters, fittings, and connectors etc. (Make : Custom made)
A.3.1 | 75 mm Dia - Outlet | Nos | 5
A.4 | Supplying, Installing & Testing of cast iron Floor Trap (150 mmx 150 mm) with Stainless Steel slotted top cover, odour water seal trap of approved make with all necessary adapters, fittings and connectors etc. (Makes : NECO or equivalent with Airport approval)
A.4.1 | 100 mm Dia - Outlet | Nos | 3
DRAINAGE SYSTEMS PIPING
A.5 | Supplying, Installing, Testing, and Commissioning of uPVC Pipe, for drainage with all necessary fittings such as bends, wye's, reducers, san tee's, double wye's, double combinations, san cross, and cleanout plugs etc, of approved make. and with all necessary supports/clamps for the above-raised floor pipes as per standards and site conditions/requirements. (Make : Astral/Supreme for Pipe and Fittings)
A.5.1 | 32 mm Dia | Mtr | 10
A.5.2 | 40 mm Dia | Mtr | 20
A.5.3 | 50 mm Dia | Mtr | 22
A.5.4 | 75 mm Dia | Mtr | 35
A.5.4 | 100 mm Dia | Mtr | 6
B | WATER SUPPLY SYSTEM
WATER SUPPLY EQUIPMENTS
B.1 | Supply, Installation, Testing & Commissioning of Electric Water Heater with safety valve arrangement and accessories like angle valve, flexible pipes, C.P bolts, screws, washers, etc. and proper supports necessary as per standards and site condition / requirements. (Make : Crompton/Bajaj or equivalent with Airport approval)
B.1.1 | 30 Liters vertical storage water heater | Nos | 1
B.2 | Supply, Installation, Testing & Commissioning of RO Filteration Unit for supplying pure filtered potable water to equipments like Combi-steamers & baking ovens, Fresh water taps & Coolers, Coffee/ Espresso machines, Dish-washers, Post-mix machines, Ice-machines, and Boiling-water taps etc. with necessary prefilters, filter cartridges, manifold heads, mounting brackets, shutoff valves, flushing valves, pressure gauges, and suitable connectors etc. Final make, model and details to be finalized by specialist vendor after examining the water test report of incoming water supply provided at site. (Make : Eco Smart/Aquaguard or equivalent with Airport approval)
B.2.1 | 15 Ltrs / Hr - Flow Rate | Nos | 5
WATER SUPPLY PIPE VALVES & ACCESSORIES
B.3 | Supply, Installation, Testing & Commissioning of Brass Ball Valve with full bore lever operated, SS ball and stem with a pressure rating of 16 Bar of approved make and with all necessary fittings. (Makes : NECO or equivalent with Airport approval)
B.3.1 | 15 mm Dia | Nos | 8
B.4 | Supply, Installation, Testing, and Commissioning of chrome plated Angle Valve with wall flange/rosette for all plumbing equipment/fixtures with a pressure rating of 16 Bar of approved make and with all necessary fittings. Including making good the wall/partition as per Architectural / Interior Design and as per relevant standards. (Makes : NECO or equivalent with Airport approval)
B.4.1 | 15 mm Dia Inlet (Outlet size to fit with plumbing eqp/fixture connection) | Nos | 19
COLD WATER SUPPLY PIPING
B.5 | Supply, Installation, Testing & Commissioning of (Chlorinated Poly Vinyl Chloride) CPVC Pipe conforming to IS 15778, ASTM D 2846, in SDR 11 Class 1, (temperature range of maximum 82°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Astral/Supreme for Pipe and Fittings)
B.5.1 | 15 mm Dia | Mtr | 25
B.5.2 | 20 mm Dia | Mtr | 25
B.5.3 | 25 mm Dia | Mtr | 35
B.6 | Supply, Installation, Testing & Commissioning of Copper Pipe conforming to BS 2871 / EN 1057, (continous operating temperature range of maximum 90°C) with all necessary fittings such as sockets, bends, elbows, tees, reducers, unions etc, and proper supports necessary as per standards and site condition / requirements. (Make : Manibhadra fittings or equivalent with Airport approval)
B.6.1 | 15 mm Dia | Mtr | 3
PIPING THERMAL INSULATION
B.7 | Supply & fixing of Pipe Insulation of 13 mm thick, with Polyethylene-based, closed-cell foam pipe insulation and polymer protective coating to prevent external mechanical damage of approved make for Hot water pipe with a operating temperature range of 0°C to 100°C, Thermal conductivity (λ) 0.038 W/m-K @ 40°C including suitable adhesives to fix the insulation to pipe. (Make : Thermax, Maxima, Fuelpac or equivalent)
B.7.1 | 15 mm Dia | Mtr | 3
GRANT TOTAL NET
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.

## FIRE
BILL OF QUANTITIES AND ESTIMATE
PROJECT: | DIAL_T1_DILLI STREAT |  |  | DATE: | 2024-01-09
|  |  |  | REV: | R0
FIRE SERVICES - WORKS BILL OF QUANTITIES AND ESTIMATE |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor has to plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. Any service penetration inside the unit has to be made good after installation, and any fire penetrations on site have to be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | FIRE SPRINKLER SYSTEM
AUTOMATIC FIRE SPRINKLER HEADS & ACCESSORIES
A.1 | Supply, Installation, Testing & Commissioning of Automatic Concealed Fire Sprinkler Heads (Quick Response) (Bulb type Sprinklers) with adjustable Escutcheon plates (Rosette plates). Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and an Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured & Certified to UL 199. Shall also include suspending arrangements with ceiling/wall etc.
A.1.1 | Concealed Pendant type of 68° C (Chrome Finish Plate Cover) | Nos | 22
A.1.2 | Concealed Pendant type of 79° C (Chrome Finish Plate Cover) | Nos | 8
A.2 | Supply, Installation, Testing & Commissioning of Automatic Fire Sprinkler Heads (Quick Response) (Bulb type Sprinklers) with Standard Temperature Response with 5mm glass bulb, Temperature rating of 68° C / 93° C, K-factor of 80, Nominal Thread size of 1/2" NPT (15mm) and a Orifice size of 13mm with a Max. Working Pressure of 12 Bar (Factory hydrostatic test pressure of 35 Bar) and to be Manufactured & Certified to UL 199. It shall also include suspending arrangements with ceiling/wall etc.
A.2.1 | Upright type of 68° C (Finishing - Chrome Plated) | Nos | 23
FIRE SPRINKLER PIPE VALVES & ACCESSORIES
A.3 | Supply, Installation, Testing & Commissioning of Cast Iron Butterfly Valve slimseal PN16 (working pressure of 16 Bar), standard flow control lever operated with stainless steel shaft & disc, seat material with Black Nitrile / EPDM, flanges nuts and bots etc.
A.3.1 | 65 mm Dia | Nos | 3
A.4 | Supply, Installation, Testing & Commissioning of Brass body Test And Drain Valve with Sight Glass, working pressure of 20 Bar (300 PSI), standard lever operated with stainless steel stem & lever, with necessary weldable fittings in position as per drawings / site conditions.
A.4.1 | 25 mm Dia | Nos | 3
A.5 | Supply, Installation, Testing & Commissioning of Flow Switch on Sprinkler distribution header pipe with a working pressure of 31 Bar (450 PSI) and a flow sensitivity range of 4-10 GPM (15 - 38 LPM) on each floor / zone / inside proposed demise area tap of point, shall be connected to fire alarm panel through cable.
A.5.1 | 65 mm Dia | Nos | 3
FIRE SPRINKLER PIPING
A.6 | Supply, Installation, Testing & Commissioning of GI "C" Class Fire Sprinkler Pipe confirming to IS: 1239 with all fittings like bends, tees, flanges, nut, bolt and washers etc, and proper pipe supports to not more than 3 meter apart of the pipe length. The pipe work shall be hydrostatically tested for not less than 2 hours at 15 Bar (or 1.5 times the working) pressure without leak. The pipes are to be applied with 2 coats of primer (indicated film thickness, dry 50 microns) and 2 coats of enamel finish paint of approved colour (indicated film thickness, dry 30 microns)
A.6.1 | 25 mm Dia | Mtr | 70
A.6.2 | 40 mm Dia | Mtr | 15
A.6.3 | 50 mm Dia | Mtr | 10
A.6.4 | 65 mm Dia | Mtr | 20
B | FIRE ALARM SYSTEM ( ADDRESSABLE TYPE )
FIRE ALARM SYSTEM - DETECTION DEVICES
B.1 | Supply, Installation, Testing, and Commissioning of Addressable Type (Optical Smoke & Heat) Multi Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make with all necessary mounting and fixing arrangements.(Above & Below Ceiling)
B.1.1 | Below ceiling level | Nos | 5
B.1.2 | Above ceiling level | Nos | 5
B.2 | Supply Installation Testing and Commissioning of Conventional Response Indicators(Below ceiling level)
B.2.1 | Below ceiling level | Nos | 5
B.3 | Supply, Installation, Testing, and Commissioning of Addressable Type Fixed Temperature Heat Detector Conforming to EN54, with standard detector mounting base, IP30 Ingress Protection, Area Coverage of 50 sq. mm (subject to local standard), 360° Angle Visibility, Operating Temperature (-10°C to +50°C), approved by LPCB, of approved make with all necessary mounting and fixing arrangements.
B.3.1 | Heat Detector - 58°C fixed temperature | Nos | 4
B.4 | Supply, Installation, Testing, and Commissioning of Addressable Type Manual Call Point Conforming to EN54 with Break glass, ABS material enclosure, IP30 Ingress Protection, Operating Temperature (-10°C to +50°C) of approved make suitable for flush and surface mounting with all necessary mounting, termination and fixing arrangements.
B.4.1 | Manual Call Point - (Wall / Partition Mounted) | Nos | 2
B.5 | Supply, Installation, Testing and commissioning of Addressable type Sounder Strobe with inbuilt Isolator & operating temp (- 10 degree to + 55 degree ) complete as required and duly approved by LPCB / EN54.
B.5.1 | Sounder Strobe - (Wall / Partition Mounted) | Nos | 2
FIRE ALARM SYSTEM - MODULE DEVICES
B.6 | Supply, Installation, Testing, and Commissioning of Addressable Type Monitor Module
B.6.1 | Monitor Module | Nos | 6
B.7 | Supply, Installation, Testing, and Commissioning of Addressable Type Control Module for shutting down FCU’s, and magnetic fire door holders. Elevator recall, fire damper, pressurization fan, strobes etc
B.7.1 | Control Module | Nos | 1
B.8 | Supply, Installation, Testing, and Commissioning of Addressable Type Isolation Module
B.8.1 | Isolation Module | Nos | 2
FIRE ALARM SYSTEM - CABLING
B.9 | Supply and surface laying of armoured FRLS twisted pair, shielded cable.
B.9.1 | 2 core 1.5 Sqmm | Mtr | LUMSUM
B.10 | Supplying, installing, testing and commissioning approved make PVC conduits on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends etc.
B.10.1 | 20 mm Dia | Mtr | LUMSUM
C | FIRE EXTINGUISHERS
C.1 | DRY POWDER STORED FIRE EXTINGUISHER
C.1.1 | Supply and fixing of 4.0 Kg ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 15683 with BIS Fire rating 2A : 21B, Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. | Nos | 4
C.2 | CO2 PORTABLE FIRE EXTINGUISHER
C.2.1 | Supply and fixing of 4.5 Kg CO2 (Carbon-dioxide) Type Fire Extinguisher. Design, construction and testing as per IS 15683 with BIS Fire rating 21B, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories. | Nos | 6
C.3 | K TYPE PORTABLE FIRE EXTINGUISHER
C.3.1 | Supply and fixing of 6.0 Ltr Class K wet chemical Type Fire Extinguisher as per BIS Fire Rating 5F. Pressurized with nitrogen gas at 10 bar and body Hydrotested at 35 bar, Operating temperature +5°C to +60°C, Supplied with standard accessories. | Nos | 4
C.4 | FIRE DETECTION TUBE SUPPRESSION SYSTEM
C.4.1 | Supply and fixing of 2.0 Kg Fire Detectin Tube Suppression Ssystem( Carbon-dioxide) Type Fire Extinguisher. Design, construction and testing as per IS 15683 with BIS Fire rating 21B, Body Hydrotested at 250 bar, Operating temperature -30°C to +55°C, |  | 1
C.5 | FIRE EXTINGUISHER MOUNTING BRACKET / MOUNTING STAND
C.5.1 | Supply and fixing of Mounting Bracket / Stand for Fire Extinguishers fabricated out of good quality S.S, Pipe / Plate & Fittings duly painted with primer and final enamel paint coat as per the regulatory authority or to match with the ID design to suit the above Fire Extinguishers. | Nos | 14
GRANT TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.