## HVAC
BILL OF QUANTITIES
PROJECT: | IN-HYD-FF46-JAIME OLIVERS PIZZERIA |  |  | DATE: | 2024-05-11
|  |  |  | REV: | R1
HVAC SERVICES - WORKS BILL OF QUANTITIES |  |  |  | STATUS: | TENDER
GENERAL NOTES :
All measurements and figures provided below are indicative only and must be confirmed by the contractor. The contractor shall have full responsibility for measurements or surveys, and no additional costs or charges will be accepted. The scope of work and quantities mentioned in the MEP BOQ pertain to the MEP services only inside the site location (e.g., within the unit demise). If any termination or connection of services is required outside the site location (i.e., connection of the unit M&E to the airport M&E or service termination to the airport external façade or roof, etc.), then the contractor must plan, design, and detail these connections in consultation with the airport. The contractor is to do all necessary site surveys to verify the optimal routing for the services in such cases. The contractor shall include in their scope end point termination of all MEP points for equipment based on supplied equipment and airport regulations, No additional costs shall be claimable for end point terminations. Any service penetration inside the unit must be made good after installation, and any fire penetrations on site must be detailed as per Airport requirements. The contractor is to verify at site and also with Airport authorities whether there are provisions at site to suit the design. Example: The contractor should check for provisions and the extent of power, plumbing, chilled water, ducting, fire, and gas provisions etc. available at the site and satisfy himself that there are no risks to the design intent.
ITEM CODE | ITEM NAME | UOM | QTY | UNIT COST | REMARKS
A | HVAC SYSTEM EQUIPMENTS
AC EQUIPMENT (CHILLED WATER - TYPE)
A.1 | Supply, installation, testing and commissioning of chilled water type High static Fan coil unit of approved make comprises with evaporator coil, high efficiency fan-motor assembly, 4RD chilled water cooling coil section, pre-filters with EU3/G4 class filters, condensate drain pan (SS 18G) duly insulated with cross linked polymer, insulated drain piping; Units shall be equipped with valve package comprises of ball valve with strainer on the inlet side and PICV with two isolation ball valves on the outlet side. The unit shall be suitable for 230 volts, 50 Hz, 1 phase AC supply with all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above with a suitably sized stainless steel insulated drip tray below the AC equipment. Fan coil units shall be selected for the lowest operating noise level. (Make: Waves, System Air, Daikin, Voltas, Caryaire,Blue Star or equivalent with airport approval)
A.1.1 | 2.5 TR - (1000 CFM @ 70-80 PASCAL -ESP) | Nos | 1
A.1.2 | 4.0 TR - (1600 CFM @ 90-100 PASCAL -ESP) | Nos | 1
KITCHEN EQUIPMENTS
A.2 | Supply, installation, testing and commissioning of Double Skinned ceiling suspended Electrostatic Precipitator(ESP) of approved make with minimum 25 mm thick panels of minimum 40 Kg/m3 density with 0.60 mm precoated GSS outer skin and 0.60 plain inner skin, including EU4 Pre Filter, ionizer, collection plate .The Unit shall be suitable for 230V, 1 Phase, 50 Hz AC supply. Auto power cut-off when door is opened, short circuit, arc protection and auto restore power supply, Quote shall be inclusive of all necessary mounting and fixing arrangements for the equipment, including hanging arrangements with vibration isolation as required based on the hanging structure above. (Make: Rydair, Trion or equivalent with airport approval).
A.2.1 | 3700 CFM | Nos | 1
B | AC PIPING AND ACCESSORIES
AC CONDENSATE DRAIN PIPE
B.1 | Supply and fixing in position of Rigid PVC condensate drain water piping with necessary supports and fittings like, U-traps, elbows, tees and reducers insulated with 9mm nitrile rubber and BOPP tape. (Make: Astral, Supreme or equivalent with airport approval).
B.1.1 | 25 mm Ø | Mtr | 18
B.1.2 | 32 mm Ø | Mtr | 4
AC CHILLED WATER PIPING
B.2 | Supply, installation and testing of MS class (C) Pre-Insulated Chilled Water Pipe of approved make with expanded polyurethane foam (PUF) insulation of 36 kg/m3 minimum density, thickness as specified below and 26 G aluminum cladding with supports and all fittings such as bends, tees, elbows, reducers, flanges, special fittings, suspension hangers, supports as applicable as per site conditions. The insulation shall completely fill the annular space between service pipe and jacket and shall be bonded to both by Cold adhesive. Rubber saddles shall be considered below supports for all the piping works. (Make:Jindal (Hissar), Tata steel, Sail)
B.2.1 | 25 mm Ø - (Insulation - 30 mm thick) | Mtr | 7
B.2.2 | 32 mm Ø - (Insulation - 30 mm thick) | Mtr | 36
C | AC PIPING VALVES & ACCESSORIES
C.1 | Supply, Installation, Testing, and Commissioning BTU Meter of approved make with direct pipe connection type or operated via sensor module connected supply and return pipe with all necessary fixing and valve arrangements. LCD display (shows all water parameters), with flow rate, temperature inputs, data storage up to 365 days. The display panel shall be mounted at readable height and it shall include interconnecting wiring between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box with all necessary fixing arrangements. Unit shall be compatible with facility Building Management System. (Make and model shall be as per Airport requirement)
C.1.1 | 32 mm Ø | Nos | 1
C.2 | Supply, Installation, Testing, and Commissioning of Pressure Independent Control Valve (PICV) with Electric actuators with selectable control modes, with a pressure rating of PN 16 of approved make with threaded or flange connection ends with all necessary fixing arrangements. (Make: Danfoss,Siemen,Flowcon,Honeywell,Anergy,Belimo,Johnsons Control )
C.2.1 | 32 mm Ø (9.6 gpm) | Nos | 1
C.2.2 | 25 mm Ø (6.0 gpm) | Nos | 1
C.3 | Supply, Installation, Testing, and Commissioning of Forged Brass Ball Valve with Y - Strainer of approved make with full bore lever operated and removable perforated SS mesh screen with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled/hot water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Rapidcool,RB,Emerald,Sant,Zoloto (It should be PN 16).)
C.3.1 | 32 mm Ø | Nos | 1
C.3.2 | 25 mm Ø | Nos | 1
C.4 | Supply, Installation, Testing, and Commissioning Forged Brass Ball Valve of approved make with full bore lever operated with a pressure rating of PN 16. Valve insulation shall be same thickness for corresponding size as chilled/hot water pipe insulation with threaded connection ends with all necessary fixing arrangements. (Make: Rapidcool,RB,Emerald,Sant,Zoloto (It should be PN 16).)
C.4.1 | 32 mm Ø | Nos | 5
C.4.1 | 25 mm Ø | Nos | 2
C.5 | Supply, Installation, Testing, and Commissioning of Analog type Pressure Gauge of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald)
C.5.1 | Dial Size - 63 mm Ø | Nos | 4
C.6 | Supply, Installation, Testing, and Commissioning of Analog type Thermometer of approved make with all necessary fixing arrangements. (Make: H.Guru, Fiebig, Emerald)
C.6.1 | Dial Size - 63 mm Ø | Nos | 4
C.7 | Supply, Installation, Testing, and Commissioning of Forged Brass Drain Valve / Drain Cock, of approved make rubber seal, O rings e with all necessary fixing arrangements. (Make shall be as per Airport requirement)
C.7.1 | Drain Valve connected in chilled water supply line | Nos | 2
C.8 | Supply, Installation, Testing, and Commissioning of Forged Brass Automatic Air Vent of approved make with all necessary fixing arrangements. (Make shall be as per Airport requirement)
C.8.1 | Automatic Air Vent connected in chilled water return line | Nos | 2
C.9 | Supply, installation, testing & commissioning of Test point of approved make with all necessary fixing arrangements. (Make shall be as per Airport requirement)
C.9.1 | Test point for supply and return lines | Nos | 4
D | AIR DISTRIBUTION DUCTS
RECTANGULAR DUCTS
D.1 | Supply, installation, and testing of Galvanized Iron (GI) factory fabricated Square / Rectagular Ducts with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, slotted rails, threaded rods, anchor bols, nuts, bots, structural beam clamps as applicable. The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
D.1.1 | 24 Gauge - (0.70 mm Thick) - Supply Air Duct | Sq.Mtr | 28
D.1.2 | 24 Gauge - (0.70 mm Thick) - Kitchen Supply Air Duct | Sq.Mtr | 12
D.2 | Supply, installation, and testing of Mild Steel (MS) Ducts fabricated with hot rolled or cold rolled black steel sheets Square / Rectagular Ducts with fully welded leak proof construction with Fire rated spay coat or painted with multiple coats of Red Oxide along with Rock wool insulation conforming to NFPA 96 Standards. with all necessary fittings, connections, vanes, flanges, bracings,gaskets,duct collars, splitter dampers, and all necessary duct supports like MS Angle bars, threaded rods, anchor bols, nuts, bolts, structural beam clamps as applicable. Duct and all other acessaries shall be fire resistant, The ducts shall be fabricated and installed in line with SMACNA or DW-144 as required by Airport / local regulatory or approval body having jurisdiction. (Make: Zeco, Ductofab, Waves, Rolastar or equivalent with airport approval).
D.2.1 | 18 Gauge - (1.31 mm Thick) - Kitchen Exhaust Air Duct | Sq.Mtr | 24
E | AIR DISTRIBUTION DUCT INSULATION & LINNING
AIR DISTRIBUTION DUCT - THERMAL INSULATIONS
E.1 | Supply, installation, and testing of Thermal Insulation of ducting using closed-cell elastomeric nitrile rubber, Black Colour with Thermal Conductivity λ - 0.036 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
E.1.1 | 19 mm thicknesses - (SAD) - External Duct Insulation | Sq.Mtr | 22
E.1.2 | 19 mm thicknesses - (KSAD) - External Duct Insulation | Sq.Mtr | 12
E.2 | Supply, installation & testing of Thermal Insulation of ducting using glass wool with silver foil covering, density 40 Kg/m3, Thermal Conductivity λ - 0.030 W/(m-K) at 0° C and Fire performance according to building regulations - Class "O" as per BS 476. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
E.2.1 | 50 mm thicknesses - (KEAD) - External Duct Insulation | Sq.Mtr | 24
AIR DISTRIBUTION DUCT - ACCOUSTIC LININGS
E.3 | Supply, installation of Acoustic Lining of approved makes for duct insulation using open cell processed elastomeric nitrile rubber, with having a density of 150 ± 10 Kg/m3 Quote shall be inclusive of necessary Adhesive. (Make: Armacell, K-Flex, A-Flex or equivalent with airport approval).
E.3.1 | 15 mm thicknesses - (SAD) | Sq.Mtr | 6
F | AIR DISTRIBUTION DUCT ACCESSORIES
DUCT AIR CONTROL DAMPERS
F.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Low Leakage square / rectangular Volume Control Damper with aero-foil opposed blades and nylon gears system outside air stream with adjustable handle with position arresting bolt. (Make: Greenheck, System Air, JCI, Caryaire or equivalent with airport approval)
F.1.1 | Size - 400 x 150 mm | Nos | 1
F.1.2 | Size - 450 x 150 mm | Nos | 1
F.1.3 | Size - 400 x 200 mm MS FLANGE | Nos | 1
F.1.4 | Size - 350 x 150 mm MS FLANGE | Nos | 1
F.1.5 | Size - 600 x 250 mm MS FLANGE | Nos | 1
F.1.6 | Size - 500 x 200 mm MS FLANGE | Nos | 1
G | AIR TERMINALS - (GRILLES, REGISTERS, DIFFUSERS & LOUVERS)
GRILLES
G.1 | Supply, installation, tetsing and commissioning of Extruded Aluminium Single Deflection Grille with opposed blade collar damper aerofoil adjustable front and rear blades with collar damper frame of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements. (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
G.1.1 | Neck Size - 750 x 150 mm | Nos | 3
G.1.2 | Neck Size - 750 x 150 mm - without damper | Nos | 5
G.2 | Supply, installation, tetsing and commissioning of Extruded Aluminium Double Deflection Grille with opposed blade collar damper aerofoil adjustable blades with of 20mm flange, Powder coated finish with RAL Colour as required by ID Designer / Architect of approved make and with all necessary fixing arrangements (Make: System Air, Caryaire, Dynacraft, Airmaster or equivalent with airport approval).
G.2.1 | Neck Size - 350 x 350 mm | Nos | 7
G.2.2 | Neck Size - 350 x 350 mm - without damper | Nos | 4
G.2.1 | Neck Size - 400 x 400 mm | Nos | 1
H | HVAC SERVICE IDENTIFICATION LABELS, SIGNS & TAGS
H.1 | All services like Ducts, Pipes need to be clearly labelled or tagged at site with service identification flow direction etc. And all equipment needs to tagged as per Airport requirements.
H.1.1 | Labelling & Tagging for Services and Equipment's | Lot | 1
J | TESTING AND BALANCING
J.1 | Air balancing of Supply, Fresh air and Exhaust air system to arrive as per design air flow rates | Lumpsum
J.2 | Water balancing of Entire Chilled Water piping system to arrive the designed flow rates. | Lumpsum
J.3 | Chilled water pipe Pressure testing at 15kgf/cm2 hydrostatics pressure for a minimum 24hrs hold time .Testing should be done in the presence of Airport Concerned Persons. | Lumpsum
GRAND TOTAL
NOTE: The quantities mentioned in the above BOQ includes services only inside the site location (building). If any termination of services required outside the site location contractor to verify at site and provide the quantity and cost over and above this BOQ. Any service penetration to be made good after installation. Fire sealing to be done for penetrations as per Airport requirement.