## Sheet1
Bangalore International Airport Limited
|  |  |  | Rev: | 0
BOQ FOR FIRE FIGHTING SYSTEMS |  |  |  | Date: | 13.11.2024
Sr. No | Description | Qty | Unit | Rate | Amount
Fire Hydrand work
1 | Dismantaling and modification of existing 80mm hydrand system as per site requiremnt | 1 | set | 20500 | 20500
a | Hose reel draum
b | 80mm butter fly valve
c | 80mm pipe and 25mm dia pipe
d | 80mm dia Hydrant valve
HVAC
1.1 | CHW FLOOR MOUNTED AIR HANDLING UNIT VERTICAL TYPE
SITC of double skin floor mounted AHU with suitable plug type fans with IE3 efficient 3phase motor, UVGI, Moisture eliminators etc. The thickness of panel to be with 42+/-3mm thick PUF Insulation. The coil shall be of hard copper tubes covered by aluminium fins with 13-15 FPI. The AHU to have a SS condensate drain tray which shall be duly insulated with 13mm thick class O nitrile rubber insulation. The contractor to furnish the GA drawings of AHU prior to ordering with necessary technical catalogues and fan curve selections. The noise level near the AHU should not cross more than 60dbA at 1m away from the unit. Also the AHU shall have a prefilter of MERV 8 with necessary framework. AHU body frame shall be with Aluminium . AHU shall have TEFC Squirrel Cage IP 55 Protected VFD Compatible induction motor, copper header, "Copper to MS" adopter, vibration isolation pad. Scope also includes limit switch with lights inside AHU.
AHUs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units. Fan outlet velocity shall not exceed 1600 FPM (8.12 MPS). Chilled water inlet & Outlet temp to be 8 & 13.5°C. AHUs shall be of following design parameters :
Capacity Tonnage ESP No. of USGPM
(Cfm) TR (mm WG) Rows
a | 11200 25 40 4/6 60 | No | 1 | 175000 | 175000
We received BOQ approval for a horizontal type, but as per the site or TDS approval, we installed a vertical type. Because of this, the supplier increased the cost