## PHE BOQ
SKY HIGH BIRYANI, DELHI -PHE BOQ |  |  |  | Rev: | R0
|  |  |  | Date: | 13.12.2024
Item No. | Description | Unit | Qty | Rate | Amount | Make
A | WATER SUPPLY PIPING
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall / floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes & necessary pressure testing Chasing finishing shall be done with 1:1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical / horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  |  | Astral / Ashirwad /supreme / Prince or Approved Equivalent
1.1 | 20 mm Dia | R.mt | 40 |  | 0
1.2 | 25 mm Dia | R.mt | 10 |  | 0
1.3 | 32mm Dia | R.mt | 5 |  | 0
1.4 | 40mm Dia | R.mt | 0 |  | 0
1.5 | 50mm Dia | R.mt | 0 |  | 0
2 | Copper pipes and tubes shall be hand tempered conforming to requirements of EN 1057 ( formerly BS 2871) Table X , half and the fittings shall confirm the EN-1254-I ( Formerly BS 864: part-02). The fittings shall be end feed capillary fittings within wall/ceiling / floor including cutting & chasing the wall/ floor, jointing, making connection to fixtures, equipment and piping with purposes made connectors, etc. including insulation of closed cell elastomeric nitrile rubber. thermal conductivity of elastometric nitrile rubber shall not exceed 0.038w/m deg K. The insultaion should have fire performance and thickness of nitrile rubber should be 9mm (for hot water piping)
2.1 | 20mm Dia | R.mt | 25
2.2 | 25mm Dia | R.mt | 5
2 | Providing & Fixing of forged brass lever operated Ball Valves (10Kg/Sq.cm). Valve shall have with unions. |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
2.1 | 20mm Dia | Nos. | 4 |  | 0
2.2 | 25mm Dia | Nos. | 0 |  | 0
2.3 | 32mm Dia | Nos. | 1 |  | 0
2.4 | 40mm Dia | Nos. | 0 |  | 0
2.5 | 50mm Dia | Nos. | 0 |  | 0
3 | Providing ,fixing, testing and commissioning Electromagnetic flow meter-flow (12 GPM-0.76 LPS) including providing & fixing matching with required accessories 16Kgs/Sq.cm). - Contractor to check existing make and provide that. |  |  |  |  | ENH/Porsh Marshal or approved Equivalent
3.1 | 25 mm Dia incoming line | Nos. | 1 |  | 0
3.2 | 32 mm Dia incoming line | Nos. | 0 |  | 0
3.3 | 40 mm Dia incoming line | Nos. | 0 |  | 0
3.4 | 50 mm Dia incoming line | Nos. | 0 |  | 0
4 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  |  |  |  | AO Smith or Approved Equivalent
4.1 | 5 L Capacity- | Nos. | 0 |  | 0
4.2 | 20 L Capacity | Nos. | 1 |  | 0
4.3 | 35 L Capacity- For shower | Nos. | 0 |  | 0
5 | Supply, installation,testing & commissioning of Stiebel Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories (Optional in pantry) |  |  |  |  | Stiebel Entron or Approved Equivalent
5.1 | 3.5kw in pantry- optional | Nos. | 0 |  | 0
5.2 | 8kw | Nos. | 0 |  | 0
5.3 | 13kw-3ph- Subject to load permits | Nos. | 0 |  | 0
6 | RO PACKAGE PLANT-Supply , installations, testing and comminissioning of ECO SMART-100 | No | 0 |  | 0 | Make- Ion Exchange/ or equivalent
7 | Supply, Installation, Commissioning & Testing for Booster pump for Ro water supply WITH FLOW SWITCH GRAVITATIONAL FLOW (top to bottom flow) with both side Sensor operations- A) 3CUM PER HR. B) HEAD: 25M, C) PHASE: SINGLE PHASE, D) PROTECTION: IP55, E) MONOBLOCK TYPE, with sensors cabling & Control panel.(Pump shall be Auto fill stop and Auto empty start mechanisam) |  |  |  |  | Grundfoss /Kirloskar / Bharat Bijli / Agasti / or Approved Equivalent
7.1 | 0.75 HP | Nos. | 1 |  | 0
7.2 | 1.5 HP | Nos. | 0
8 | Supply, Installation of sintex loft mounted water tank of 50 Ltrs | Nos. | 0 |  | 0 | Sintex
9 | P/F water level Indicator on loft water tank by means of a transparent clear tube fixed along height of the water tank hence making water level visible | Nos. | 0 |  | 0
10 | Providing & Fixing Brass Non Return Vavles of ISI mark. Rates are for BRASS valves |  |  |  |  | Make – KITZ / ZOLOTO / AUDCO /or Approved Equivalent
12.1 | 20mm | Nos | 2
12.2 | 25mm | Nos | 2 |  | 0
12.3 | 40mm | Nos. | 0
11 | SITC of Eco smart RO-50 with all required accessories | Nos | 0 |  | 0 | Iron Exchange or Approved Equivalent
12 | SITC of standalone Ro -12 lit with all required accessories | Nos | 0 |  | 0 | Iron Exchange or Approved Equivalent
13 | SITC of ACO grease trap -model Lipumobil 0.8 -Capacity -48 lit ( 0.8 LPS) with all required accessories ( Order shall be placed as per space available below the counter) | Nos | 0 |  | 0 | Aco or Approved Equivalent
14 | SITC of ACO grease trap -model Lipumobil S -Capacity -32 lit ( 0.5 LPS) with all required accessories | Nos | 0 |  | 0 | Aco or Approved Equivalent
15 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 14 ( 25. lit) | Nos. | 1
16 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 8 ( 15 lit) | Nos. | 2
A | SUB TOTAL OF A |  |  |  | 0
B | DRAINAGE
1 | UPVC-SWR pipes (working pressure 10kg/cm2) conforming to IS 13592/92 and IS 14735-type-B solvent posted ( for Dia above 50mm) and for ( Dia below 50mm) shall be as per IS 4985 and 7834 Class-05 (10 kg/cm2) including cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of nesessary items] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] |  |  |  |  | Supreme / Finolex / Prince / Oriplast / or Approved Equivalent
1.1 | 40mm Dia | R.mt | 5 |  | 0
1.2 | 50mm Dia | R.mt | 5 |  | 0
1.3 | 65mm Dia | R.mt | 0 |  | 0
1.4 | 75mm Dia | R.mt | 10 |  | 0
1.5 | 100 mm Dia | R.mt | 15 |  | 0
1.6 | 150 mm Dia | R.mt | 0 |  | 0
2 | Supply, Install PVC Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 1 |  | 0
3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 5 |  | 0
4 | Supply, Install PVC urinal Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0 |  | 0
5 | Supply, Install PVC P- Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0 |  | 0
6 | Supply, Install PVC clean out plug including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0 |  | 0
| SUB TOTAL OF B |  |  |  | 0
C | SANITARY AND C. P. FITTINGS & FIXTURES
Supply & installation, testing and commissioning of sanitary and C.P. fittings( Client /Architect to select the model no as required and provide fixtures)
1.1 | EWC with seat cover | Nos | 0 |  | 0
1.2 | Concealed flush tank | Nos | 0 |  | 0
1.3 | Concealed flush valve | Nos | 0 |  | 0
1.4 | Health Faucet | Nos | 0 |  | 0
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0 |  | 0
1.6 | Bided | Nos | 0 |  | 0
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0 |  | 0
1.8 | Wash Basin Cock | Nos | 0 |  | 0
1.9 | shower and mixer | Nos | 0 |  | 0
1.1 | Jet Spray | Nos | 0 |  | 0
1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0 |  | 0
1.12 | Under Counter Sink including waste Coupling | Nos | 4 |  | 0
1.13 | Sink Pillar Cock - Jaquar continental series | Nos | 4 |  | 0
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 4 |  | 0
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection Jaquar continental series | Nos | 12 |  | 0
1.16 | Urinal | Nos | 0 |  | 0
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 0 |  | 0
0
| SUB TOTAL -C-SANITARY AND C. P. FITTINGS & FIXTURES ( ONLY INSTALLATIONS) |  |  |  | 0
D | S.S. GRATING
Supply , installations/ testing and commissioning of S.S.Gratings
1 | Supply installation of S.S Grating size, 450mm x 200mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) Entire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 2
2 | Supply & installation of S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 0
3 | Supply & installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS Closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. ( at hook up point)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 1
SUB TOTAL -D-S.S. GRATING INSTALLATION
GRAND - TOTAL A , B, C AND D
NOTES :
1. Taxes and duties shall be Extra as actual
Water Supply: General comments
Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.
Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter and water meter power supply should be on UPS source.
General Guidelines (Water Supply) .
Water supply pipe laying for FOH, should be laid in niche with openable cover, for BOH it could be exposed.
Supply Line installation check & leakage testing to be done, before connection with DIAL tapping point.
Specification for Supply pipe- 1) CPVC ASTM D-2846 SDR-11 Class-1, CPVC solvent ASTM F-493 for normal water
For Hot water: Copper pipe EN 1057 with thermal insulation. Thermal insulation shall be conforming to BS 476 Part 6&7 FM approved, Fittings BN-1254-1,
Pipe installation in walls (except washroom and shower room) shall be through niches with openable SS cover.
All materials/items to be used at site are subjected to prior inspection and approval from DIAL Engg. Data sheet with respect to all material need to be submitted for prior approval.
Test certificate with respect to all material need to be submitted prior to installation during MIR Process.
Make– Astral/Supreme for Pipe and Fittings.
· All pipes should be installed freely from ceiling void area. Water Supply piping from floor is not allowed. Piping drops from ceiling inside BOH areas are recommended to be exposed on walls/partitions. In FOH areas, piping drops from ceiling can be installed through niche in walls with openable S.S. covers. Needs to be mentioned in drawing.
· Existing Water Meter should be easily accessible.
· Hydro-testing of pipe to be done at a pressure of 15Kgf/cm² for 24 hrs and get it inspected from DIAL- Engg
Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter. Kindly share section drawing of same and water meter power supply should be on UPS source.
Data Sheet, material inspection & Catalogue needs to be submitted for prior approval from DIAL-Engg.
Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.
General Guidelines (Drainage) . To be followed during execution work
Grease trap Make shall be as per TDM and selection and backup calculation shall be as per TDM and have adequate space for opening of top cover for maintenance. Kindly share the details.
Cleanout provisioning for maintenance and cleaning purpose to be provided.
Water proofing for wet & Dry to be done as per TDM/Airport guideline.
Pipe laying to be done within trench, and trench flooring should have openable cover.
Power to be provided for existing Digital Water meter.
Drain Line testing to be done, before connection with DIAL tapping point.
Required JB/Openable trench cover/Grating/Floor trap/IC to be provided.
Specification for Drain Pipe- uPVC IS:4985 Class 5 & IS:7834 Class 5 for fittings, uPVC solvent- ASTM D-2564, Makes – Astral/Supreme for Pipe and Fittings.
Pipe installation in raised flooring should be through trench with openable cover.
Each and every drain should go through Grease Traps. Only Condensate drain of HVAC Units are allowed to be conned without Grease Trap. Calculations w.r.t drain flow rate with grease capacity need to be submitted w.r.t selection of Grease Traps Capacities. Only S.S. Grease Traps are allowed. Data Sheet & Catalogue needs to be submitted for prior approval from DIAL-Engg.
Size of IC should not be less than 600MMx600MM. S.S. grating with dia 5mm holes should be permanently welded inside IC at discharge end.
Y- Connections to be provided instead of Tee in uPVC waste pipe.
Note-
Before execution, all Material inspection to be done along with TDS & required test certificates.
Installation check to be done, before closing of ceiling & Flooring
Post completion of onsite work, As Built Drawing to be submitted.
DIAL Shared Guideline to be followed

## General Notes
GENERAL NOTES
1 | The items given in this schedule are provisional. The Contractor shall be paid for the actual quantity of work executed as measured at the site at the rates tendered. The Owner reserves the right to increase or decrease any of the quantities, or to ommit totally any item of work. Any claim by the Contractor on these accounts will not be entertained.
2 | All the items of work given in this schedule of quantities shall be executed strictly in accordance with the latest Indian Standard Specifications.
3 | The Contractor shall visit the site and shall satisfy himself as to the conditions under which the work is to be performed. He shall also check and ascertain the location of any existing structure or equipment or any other situation which may affect the work. No extra claim as a consequence of ignorance or on ground of insufficient description will be allowed at a later date.
4 | All equipment and material shall be IS approved.
5 | All approvals shall be obtained from Owner / Consultant
6 | All equipment and material shall be inspected at manufacturer’s works as per relevant IS by the Owner or his representative before despatch to site.
7 | All vendor drawings shall be approved by the Owner/Consultant before fabrication work starts.
8 | All Testing and Commissioning shall be as per relevant details covered in the specifications. All these testing records are to be maintained and submitted for Owner / Owner’s representative.
9 | All items of work under this Contract shall be executed strictly to fulfill the requirements laid down under “Basis of Design” in the specifications. Type of equipment, material specification, methods of installation and testing and type of control shall be in accordance with the specifications, approved shop drawings and the relevant Indian Standards, however capacity of each component and their quantities shall be such as to fulfill the above mentioned requirement.
10 | The unit rate for all equipment or materials shall include cost in INDIAN RUPEES (INR) for equipment and materials including all taxes and duties and also including forwarding, freight, insurance and transport into Contractor’s store at site, storage, installation, testing, balancing, commissioning and other works required.
11 | The rate for each item of work included in the Schedule of Quantities shall, unless expressly stated otherwise, include cost of :
a | All materials, fixing materials, accessories, appliances tools, plants, equipment, transport, labour and incidentals required in preparation for and in the full and entire execution, testing, balancing, commissioning and completion of work called for in the item and as per Specifications and Drawings.
b | Wastage on materials and labour.
c | Loading, transporting, unloading, handling/double handling, hoisting to all levels, setting, fitting and fixing in position, protecting, disposal of debris and all other labour necessary in and for the full and entire execution and for the job in accordance with the contract documents, good practice and recognize principles.
d | Liabilities, obligations and risks arising out of Conditions of Contract.
e | All requirements of Specifications, whether such requirements are mentioned in the item or not. The Specifications and Drawings where available, are to be read as complimentary to and part of the Schedule of Quantities and any work called for in one shall be taken as required for all.
f | BOQ shall be read in conjuction with technical specification, drawings,In the event of conflict between Bill of Quantities and other documents including the Specifications and drawings, the most stringent shall apply. The interpretation of the Consultant/Project Manager shall be final and binding.
12 | The Contractor shall procure and bring Materials/Equipment to the site only on the basis of drawings approved for construction and shop drawings and not on the basis of Bill of Quantities which are approximate only. This also applies to the Contractor’s requisition for Owner supplied materials.
13 | The contractor shall cooperate with all trades and agencies working on the site. He shall make provision for hangers, sleeves, structural openings and other requirements well in advance to prevent hold up of progress of the construction schedule. All supports to the civil structure shall be provided with anchor fasteners.
14 | On award of the work, contractor shall submit a schedule of construction in the form i.e BAR chart for approval of the Project Manager.
15 | On award of the work the contractor shall be issued three (3) sets of consultant’s drawings. The drawings shall be the basis of contractor’s shop drawings.
16 | Shop drawings are detailed working drawings coordinated with other trading work, which incorporate the contractor’s details for execution of the work and incorporate equipment manufacturer’s details and dimensions to ensure that the same can be installed in the space provided.
17 | All shop drawings will be made on AutoCAD and colored prints has to be produced for site work.
18 | This Schedule shall be fully priced and the extensions and totals duly checked. The rates for all items shall be filled in INK including NIL items.
19 | No alteration whatsoever is to be made to the text or quantities of this Schedule unless such alteration is authorised in writing by Consultant. Any such alterations, notes or additions shall, unless authorized in writing, be disregarded when tender documents are considered.
20 | In the event of an error occurring in the amount of the Schedule, as a result of wrong extension of the unit rate and quantity, the unit rate quoted by the tenderer shall be regarded as firm and the extensions shall be amended on the basis of rates.
21 | Any error in totaling in the amount column and in carrying forward total shall be corrected. Any error, in description or in quantity, omission of items from this Schedule shall not vitiate this Contract but shall be corrected and deemed to be variation required by the Consultant/Project Manager.
22 | Rates have been called for a number of items of works, as alternatives which, for the present do not form part of the total value of tender. However the rates for these items shall be quoted, with due care so that in the event of choice of an alternative item of work, said rate shall form part of the contract and shall not violate the contract any way.
23 | The contractor shall , from time to time, clear away all debris and excess materials accumulated at the site failing which the same shall be done by Project Manager at contractor’s risk and cost and cost of clean up shall be deducted from the contractors prorata bill.
24 | After the devices and equipment have been installed and commissioned, contractor shall cleanup the same and remove all plaster, paints, stains, stickers and other foreign matter or discoloration leaving the same in a ready to use condition.
25 | On completion of all works, contractor shall demolish all stores, remove all surplus materials and leave the site in a broom clean condition, failing which the same shall be done by the Project Manager at the Contractor'’ risk and cost. Cost of the cleanup shall be deducted from the contractor’s bills on pro-rata basis in proportion to his contact value.
26 | Provision for scaffolding if any required at site , contactor shall need to be provided.
27 | Remove existing drain and water supply lines which are not required. Clean the site for new installations.