## FIRE ALARM BOQ
ADDRESSABLE FIRE ALARM BOQ FOR CARL JR @ LUCKNOW
DATE: 17.01.2024
SR.NO | DESCRIPTION | UNIT | TOTAL QTY. | SUPPLY RATE | INSTALLATION RATE | TOTAL RATE | TOTAL AMOUNT IN RS.
A | ADDRESSABLE FIRE ALARM SYSTEM - NOTIFIER MAKE
1 | Analog Addressable Fire Alarm Control panel with battery back up for 24 hours normal operation and 15 minutes alarm operation. The control panel, battery charger etc. The panel shall be with 1 loop and expandable upto 2 loop capacity. The Fire Alarm Control Panel shall include a full featured operator interface control and annunciation panel that shall include a backlit 640-character liquid crystal display, individual, color coded system status LEDs, and a QWERTY style alphanumeric keypad for the field programming and control of the fire alarm system. Number of Loops / Fire alarm panels should be worked out based on loop capacity, It shall be selected keeping atlest 20 addresses as spare capacity in each loop. The control panel shall be capable of network expandable upto multiple panels. The panel & all devises should be FM approved and comply UL 864 or equivalent. The enclosure shall also be UL listed or equivalent The quoted rate shall include supply of necessary software and harware for progamming the panel with all necessary licence. Should have the Facility to get integrated with the MAIN FAS Panel of the Building. Electrical main LT panel, (PRO).Connecting to BMS on Bacnet or TCP/IP. | Nos | 1
i) Each loop with Min. 125 Devices & Detectors modules connection capability of Addressable FACP) 2 Loop Panel.
ii) FACP with all in-built modules & displays.
iii) 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working.
iv) Programming & setting up
v) system to be capable of operating the system for 2 hours during an emergency condition including all necessary software for remote programming of fire alarm system through central control station.
3 | Detectors and Devices
3.1 | Supply,Installation,Testing & Commissioning of Analogue Addressable Monitor module having Rotary, decimal addressing system for monitoring the field devices & shall be capable of providing DPDTcontact rated at 24V DC, 2A. | Nos | 1 |  |  | 0 | 0
3.2 | Supply,Installation,Testing & Commissioning of Analogue Addressable Relay module having Rotary, decimal addressing system and shall be capable of providing DPDTcontact rated at 24v DC, 2A. | Nos | 1 |  |  | 0 | 0
3.3 | Supply,Installation,Testing & Commissioning of wall / ceiling mounted Horn cum Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication and necessary accessories including back box. | Nos | 2 |  |  | 0 | 0
3.5 | Supply,Installation,Testing & Commissioning of above / below ceiling mounted Analogue Addressable Flash scan Type Photoelectric smoke detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 4 |  |  | 0 | 0
3.6 | Supply,Installation,Testing & Commissioning of above / below ceiling mounted Analogue Addressable Heat / Thermal detectors having Rotary, decimal addressing system with standard base, built in isolation function and junction box. The detector shall be capable to address in the range of 1-159. The detector shall be with Visible bi-color LEDs for 360 deg viewing and shall blink green every time the detector is addressed, and illuminate steady red on alarm. | Nos | 2 |  |  | 0 | 0
3.7 | Supply,Installation,Testing & Commissioning of Addressable Break Glass Manual Call Point having Rotary, decimal addressing system and having an integrally mounted addressabla module that monitors and reports contact status. | Nos | 2 |  |  | 0 | 0
4 | Response indicator. | Nos | 5
NOTE: FIRE PANEL SHALL BE PROVIDED WITH FACILITY TO INTEGRATE WITH AIRPORT PANEL
5 | CABLES
Supplying, laying, testing and commissioning of 1100V grade FIRE RESISTANCE LOW SMOKE multicore, round type, insulated, sheathed, flexible copper conductor control cables with Including necessary end terminations with copper lugs, junction box, crimping identification tags at each end etc.,) RED COLOUR ONLY (MAKE: RR CABLE)
a | 2 core x 1.5 Sq.mm armoured cable(Un-screened, LSZH armoured) | Mtr | 150 |  |  | 0 | 0
| TOTAL FOR ADDRESSABLE FIRE ALARM SYSTEM | [5 empty] | 0