## SUMMARY
CARL JR @ LUCKNOW
SUMMARY FOR ELECTRICAL WORKS
DATE : 23.01.2024
Sr. No. | DESCRIPTION |  | TOTAL AMOUNT IN Rs.
I | PANEL & SWITCHGEAR | Rs. | 0
II | UPS | Rs. | 0
III | DISTRIBUTION BOARDS | Rs. | 0
IV | CABLES & ACCESSORIES | Rs. | 0
V | WIRING & ACCESSORIES | Rs. | 0
VI | LIGHTING FITTINGS INSTALLATION | Rs. | 0
VII | EARTHING | Rs. | 0
VIII | MISCELLANEOUS | Rs. | 0
IX | LOW VOLTAGE SYSTEM (WIRING)
A | DATA AND TELEPHONE SYSTEM | Rs. | 0
| SUB TOTAL AMOUNT IN RS. | Rs. | 0
TAXES EXTRA AS APPLICABLE

## ELE BOQ
CARL JR @ LUCKNOW
ELECTRICAL BOQ
DATE : 23.01.2024
SR. No | DESCRIPTION | TOTAL QTY. | UNIT | UNIT RATE | TOTAL AMOUNT
I | PANEL & SWITCHGEAR
1 | Supply, installation, testing & commissioning of free standing, floor mounting compartmentalized panels fabricated out of CRCA sheet steel sections after carrying out 7 tank cleaning process and duly powder coated using Siemens Grey Shade No. RAL 7032. The frame structure, doors and gland plates shall have 2.0 mm thick sheets and partitions shall be with 1.6 mm thick CRCA sheet. Base channel size 75 x 40 x 6 mm of ISMC shall be provided. The panel shall be dust and vermin proof with neoprene gasket. The doors shall be provided with concealed hinges and with brazing wherever required to avoid deformation and shall be earthed. The bus bar shall be of tinned Copper with epoxy supports and shall be insulated with colour coded heat shrink sleeves. The control wiring min. 2,5 Sq.mm shall be ZHLS type. The Panel shall be provided with CTs, phase indication lamps, meters, relays and all switchgear, etc. as per the SLD. The panel shall be complete in all aspects as per the final approval of the Consultant. All componants for Switchgears shall be L&T/Legrand
a | Providing & installing MAIN LT PANEL as per SLD & Spec.: | 1 | Set |  | 0
100 Amps 4 pole, 25kA MCCB as a Incomer with overload, short circuit & Earth Fault protection, Energy manager with RS485 port for BMS connectivity & 4A with SP MCB with 100/5A-3 Nos., 15VA, CL-1 CT's for metering & of AE make and phase indicating lamps Vaishno make with SPMCB
| Busbar chamber - 1 set, 4 pole 200A Tinned AL. Busbar with necessary | 1
OUTGOINGS:
i. | 32A 4P MCB – 1 Nos.
ii. | 40A 4P MCB – 2 Nos.
iii. | 63A 4P MCB – 5 Nos.
iv. | MPCB suitable for 2.2kW-1 Nos.
v. | MPCB suitable for 2.2kW-1 Nos.
2 | Supply, installation, testing & commissioning of Switchgears.(Standard Product)
b | Supply,Installation,Testing and Commissioning of 32 Amps,4Pole MCB for HVAC Outdoor Isolation all complete with mounting accessories IP 65 | 1 | Nos. |  | 0
d | Supply & installation of DOL starter L&T/Siemens/Legrand for 3 kW load | 2 | Nos.
i | Supply & installation of DOL starter as per Type-2 Coordination for 2.2 kW (3.0HP) load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For AHU) | 1 | Nos.
j | Supply & installation of DOL starter as per Type-2 Coordination for 1.5 kW (2.0HP) pump load with on / off / trip indication Lamp, on off push button, & phase indication Lamp .(For Scrubber) | 1 | Nos.
m | 32 amps 4P MCB with 32A 5 Pin Ray Roll Socket complete with all mounting accessories – for Kitchen Legrand make model No. 6078 80 | 3 | Nos.
p | 20A Rey roll socket complete with 32 amps DPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | 13 | Nos. |  | 0
q | 5/15A Rey roll socket complete with 15 amps SPMCB with 3 pin metal clad socket - Legrand make Model No. 6078 41 | 22 | Nos.
3 | SITC of Standalone Gas leak detector with inbuilt sounder for Kitchen | 3 | Nos.
| TOTAL FOR MAIN PANEL & SWITCHGEAR |  |  |  | 0
II | INVERTER / UPS
1 | Supply, Installation, testing and commissioning of 15 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. | 1 | Nos |  | 0
| TOTAL FOR UPS |  |  |  | 0
III' | DISTRIBUTION BOARDS
Supply, installation, testing & commissioning of Distribution Boards surface / flush mounted with Double door containing MCB/ELMCB as incomer and SPMCB as outgoing. All MCBs are of 10KA breaking capacity and ELMCBs/RCCB should be of 30mA/100 mA sensivity. The DB shall have appropriate no. of top and bottom knock outs for outgoing circuits and shall be complete with necessary busbars, interconnection terminals and earth studs. All terminations in DB shall be complete with ferulling, dressing and all circuits shall be properly labeled with PVC strip (sticker type) having identification as per the final approval of Consultant. For UPS DB MCB shall be 'D' type and other MCBs shall be 'C' category for lighting and raw power DB LEGRAND/L&T
1 | Lighting Distribution Board - LPDB | 1 | Nos. |  | 0
12 WAY TPN DB
I/C- 1 # 63A FP MCB , 16KA
SUB I/C - 3 # 40A DP RCCB 30mA per phase
O/G - 24 # 10/16A SP MCB
3 | Kitchen Power DB - (KPDB1) | 1 | Nos. |  | 0
12 WAY TPN DB
I/C- 1 #63 A FP MCB
SUB I/C- 3#63 DP ELCB 100mA per ph
O/G - 24 # 16/20A SP MCB
4 | UPSDB | 1 | Nos. |  | 0
16 way SPN DB
Incomer: 63A DP RCBO 30mA
Outgoings :10/16 SP MCB, 'D' Type – 10 Nos
| TOTAL FOR DISTRIBUTION BOARDS |  |  |  | 0
IV | CABLES & ACCESSORIES
Supply & installation of following LT XLPE FRLS cables (FINOLEX/RR KABLE/POLYCAB) rated for 600 / 1100 volts AC as per IS standard 1554 Part 1 with necessary M.S. clamps. All cables shall be properly clamped or tied when run on cable trays. All such cables shall be provided with temporary labelling at every 20 mtrs and ten finally with metal identification tags showing the size and the location from/to the specific Panel/DB at both ends.
5 | 3.5C x 120 Sq. mm A2XFY - MAIN PANEL | 80 | Mtr.
9 | 3.5C x 35 Sq. mm A2XFY | 100 | Mtr.
10 | 4C x 16 Sq. mm A2XFY - LPDB, KPDB | 50 | Mtr. |  | 0
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) Kitchen equipment | 70 | Mtr. |  | 0
17 | 3C x 6sq. mm YWY cable ( Cu ) UPS & UPSDB | 30 | Mtr.
18 | 3C x 4sq. mm YWY cable ( Cu ) - AHU | 50 | Mtr. |  | 0
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | 80 | Mtr.
B | Termination of following sizes of cables with Single compression cable gland.(COMET/BRAKO)
5 | 3.5C x 120 Sq. mm A2XFY - MAIN PANEL | 2 | Nos.
9 | 3.5C x 35 Sq. mm A2XFY | 2 | Nos.
10 | 4C x 16 Sq. mm A2XFY - LPDB, KPDB | 8 | Nos. |  | 0
15 | 4C x 4 Sq. mm 2XFY Cable ( Cu ) Kitchen equipment | 8 | Nos.
17 | 3C x 6sq. mm YWY cable ( Cu ) UPS & UPSDB | 4 | Nos.
18 | 3C x 4sq. mm YWY cable ( Cu ) - AHU | 2 | Nos. |  | 0
19 | 3C x 2.5 Sq. mm YWY cable ( Cu ) | 8 | Nos.
| TOTAL FOR CABLES & ACCESSORIES |  |  |  | 0
V | WIRING & ACCESSORIES
Notes :
1) Rates for point wiring shall include supply & installation of Wires & wiring acccessories such as angle holders/ceiling roses as required. conduits, conduit accessories such as junction boxes, Ts, elbows etc,Switches, sockets & fixtures shall not be included in the point wiring rates. These will be counted & paid separately.
2) Unless otherwise specified, all wires in point wiring shall be 2.5 sq.mm
Stranded copper conductor 1.1 KV grade, I.S.I. marked (P+N+E),
LSZH) PVC insulated .
Wires shall be colour coded (Red, Yellow and Blue for Phases,
Black for Neutral & Green for earth).
3) Looping of wires shall be in fittings and switch boxes only
4) Location of switches/sockets/ DBs shown on the drawings shall
be confirmed with the Architect/ Consultant/ Project Manager
before installation.
5) All Surface and concealed Conduits shall be rigid GI conduits of
size not less than 20 mm dia as per applicable IS.
6)The Contractor can take more than one circuit in the same conduit
provided they are of the same phase. The size of conduit shall be
decided according to the number of wires in it as per applicable IS & as
specified.
7) Payments for light fixtures & fans will be made separately as per the
items given in 'Light Fixtures & Accessories'.
8) Type & location of light fixtures shown in the drawings are
tentative and subject to revision as per the recommendation of
Architect/ Consultant. The quantities (number of points and accessories)
of point wiring will be revised as actual installed on account of such
revisions in the layouts.
9) Circuit wiring from DBs to the switch boards or first light point shall
Be included as primary points & remaining points of the same looping
shall be considered as Secondary points and shall be counted in nos.
10) Circuit Wiring from DB to Kitchen Power points shall be measured in running meters
1 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of GI conduits and accessories shall be included.
Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | 10 | Nos. |  | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | 15 | Nos. |  | 0
2 | Supply, installation, testing & commissioning of point wiring for light points, power points. Point wiring for primary point shall include wiring from Switch Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same switch board where primary points are controlling. The Power points shall be measured in Nos. Cost of FRLS PVC conduits, 6A switch & switch board and accessories shall be included.
a) | Primary Light points controlled by Switch (3R x 2.5 sqmm wire) | 6 | Nos. |  | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | 10 | Nos. |  | 0
c) | DB to SB & SB to SB circuit wiring : For Switch Operated Primary point @ SB to SB loop point. Wiring for switch board controlled by MCB already installed in DB by using 3 X 2.5 sq. mm flexible LSZH copper wires in 25mm GI conduits as per IS 9537 part-3 or surface mounted. | 30 | Mtrs |  | 0
3 | Supply, installation, testing & commissioning of point wiring for Emargency light points, power points. Point wiring for primary point shall include wiring from Distribution Board upto First point of the circuit and shall be measured in nos. Secondary points shall also be measured in nos and shall include the remaining light points of the circuit controlled from same distribution board where primary points are controlling. The Power points shall be measured in Nos. Cost of FRLS PVC conduits and accessories shall be included.
Averagepoint length of primary&secondaryto be derived by Contractor, fromthe drawing provided AND+/-1MtrMeasured Radially
a) | Primary Light points controlled by MCB (3R x 2.5 sqmm wire) | 1 | Nos. |  | 0
b) | Secondary Light points looped in the same circuit. (3R x 2.5 sqmm wire) | 1 | Nos. |  | 0
5 | Providing point wiring for Raw Power points 1no. 6/16A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 4.0 sq. mm copper conductor wires and minimum 4.0 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of FRLS PVC Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be LSZH type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | 30 | Nos. |  | 0
b) | Secondary points | 22 | Nos. |  | 0
6 | Providing point wiring for Raw Power points 1no. 6A switch socket outlet on Skirting level to be looped from the nearest point using 2 x 2.5 sq. mm copper conductor wires and minimum 2.5 sq. mm copper conductor PVC insulated green colour earth wire as per approval of Architect / Consultant. (Cost of Conduit / Floor Raceway and switch sockets are considered elsewhere). ( Wires shall be FRLS type ) Note: Average primary / secondary point length to be derived by Contractor, from the drawing / site provided AND +/- 1 Mtr Measured Radially.
a) | Primary Point | 4 | Nos.
b) | Secondary points | 8 | Nos.
8 | Supply and laying of following PVC insulated copper conductor 1100 volt grade stranded flexible LSZH wire in already laid GI conduit concealed or surface mounted making connections where ever required to complete the installation.(For Kitchen and Bar Power Points) Conduit rate shall be paid separately.
a) | 2R x 2.5Sqmm + 1R x 2.5Sqmm Cu. Wires | 180 | Mtr. |  | 0
b) | 3R x 4Sqmm Cu. Wires | 250 | Mtr. |  | 0
c) | 4R x 4Sqmm + 2R x 2.5Sqmm Cu. Wires | 50 | Mtr. |  | 0
d) | 4R x 6Sqmm + 2R x 2.5Sqmm Cu. Wires |  | Mtr. |  | 0
9 | Supply & installation of 25 mm dia. GI conduit with pull box / junction box & all accessories for Kitchen & Bar Power wiring as per the requirement
a | - do - but conduit pipe shall be Rigid type. | 100 | Mtr. |  | 0
b | - do - but flexible conduit pipe | 30 | Mtr. |  | 0
12 | Supply and installation of GI trunking (SV POWER/ASIAN) with 2 mm thickness & properties/clamps for suspension at appropriate intervals & as per the route approved by Architect/Consultant. (For DATA/CONTROL WIRING/LIGHTING & POWER CIRCUITS / KITCHEN)
a | 300 x 50 x 2mm | 30 | Mtr.
d | 100 x 50 x 2mm | 20 | Mtr.
15 | Supply, installation, testing & commissioning of flush mounted plate type switch and switch + sockets with hot dipped GI box complete as per the final approval of Architect/Consultant
a | 6A one way plate type switch | 6 | Nos. |  | 0
c | 5/15A 5pin switch socket outlet & usb point | 10 | Nos. |  | 0
f | 3 nos. 5/15A socket controlled by 2no 6A switch+ data+telephone+usb | 3 | Nos.
g | 2 nos. 5/15A socket controlled by 2no 6A switch + data | 15 | Nos.
l | I phase, 2 Nos x 5/15 amp, bakelite socket & switch, housed in Fabricated SS Panel suitable for hanging arrangement for Kitchen equipments. (having Two outlet /6 modular plate) | 1 | Nos. |  | 0
17 | Supply, installation of temporary lighting & power arrangement for construction purpose of with industrial type switch & sockets/MCB's/ELCB's & lighting fittings as required to finish the work for interior contractor & necessary electrical protections throughout the site for construction work till the handover of site. Contractor shall maintain the saftey rules & regulations as per Airport Security Department. The material shall be taken back by the contractor. | 1 | Job |  | 0
| TOTAL FOR WIRING & ACCESSORIES |  |  |  | 0
VI | LIGHTING FITTINGS
Installation, testing & commissioning of the following concealed / surface mounted or suspended light fixtures AS PER FINAL APPROVAL FROM ARCHITECT/CLIENT/CONSULTANT with lamps, ballast & all necessary mounting & supporting accessories. No additional cost shall be paid for supporting.
0
1 | 600x600mm PANEL LIGHT | 18 | Nos. |  | 0
2 | 1200mm SOFFIT LIGHT | 7 | Nos. |  | 0
3 | DOWNLIGHT | 8 | Nos. |  | 0
4 | 1000MM TRACK LIGHT | 20 | Mtr. |  | 0
5 | 2000MM TRACK LIGHT | 6 | Mtr. |  | 0
6 | 1400x2100MM SOFFIT LIGHT | 2 | Nos. |  | 0
7 | LED STRIP LIGHT | 35 | Mtr. |  | 0
| TOTAL FOR LIGHTING FIXTURES |  |  |  | 0
VII | EARTHING
3 | Supply & erection of G.I. strip of 25 x 3 mm used for earthing on wall, cable trays with necessary clamps fixed on wall painted with bituminous paint in an approved manner. | 60 | Mtr. |  | 0
4 | 1 no. 4 sq. mm YY cable in 25mm GI conduit for earthing FOR NETWORK RACK | 20 | Mtr. |  | 0
5 | Supplying & erecting bare copper conductor of 8 swg for earthing purpose | 60 | Mtr.
| TOTAL FOR EARTHING |  |  |  | 0
VIII | MISCELLANEOUS
4 | Supply & laying of Rubber Mats, CPRI tested conforming to standards like BS 921, ASTM-D 178 & IEC 479 for different operatng voltage ratings as below.
| Supply of 2M x 1M Rubber mat suitable for operatng voltage upto 1.1 KV | 1 | Set |  | 0
5 | Supply & fixing of approved shock treatment chart written in English and in local Language. The chart shall be framed in Teakwood and covered with glass. | 1 | Nos. |  | 0
7 | Supply & fixing of the best quality LT Danger Boards(415V) for of approved shape and size as specified by the local electrical authorities written in English, and local Language | 1 | Nos. |  | 0
8 | Supply & handed over to client of First Aid Box | 1 | Set
9 | SITC of Emergency Exit signage (battery operated) approval by client / architect / consultant. Make: Prolite or Equivalent | 2 | Nos.
| TOTAL FOR MISELANIOUS |  |  |  | 0
IX | LOW VOLTAGE SYSTEM
A | DATA AND TELEPHONE SYSTEM
1 | Supply & Installation of 25mm.dia. GI conduit with pull box/ junction box & all accessories for DATA /VOICE/WIFI wiring as per the requirement. | 300 | Mtr. |  | 0
2 | Providing DATA wiring inside 25mm dia GI conduit from each Data outlet to ICT CP Point by using Indoor Type CAT6A, | 300 | Mtr. |  | 0
3 | Supply & Installation of Internet Jack Unit RJ-45 suitable for CAT6A | 23 | Nos. |  | 0
4 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 3 Feet | 24 | Nos. |  | 0
5 | Supply & Installation of make Cat 6A, UTP Patch Cords, with snagless boots, color matched, Blue, 7 Feet | 4 | Nos. |  | 0
6 | Supply & laying indoors multi-pair 0.5mm dia copper PVC insulated and sheathed, armoured telephone cables on walls, ceiling, cable trays, trunking complete with clamps, cable markers etc. from MDF to the various tag blocks as specified
a | 10 pair cable armoured | 60 | Mtr. |  | 0
7 | Supply & installation of telephone tag block with KRONE terminal connectors, G.I.J.B as specified & com-plete with all interconnections and jumper connections bet-ween the two tag blocks on all floors as shown on drgs.
c | 10 pair tel. tag block | 3 | Nos.
| TOTAL FOR DATA AND TELEPHONE SYSTEM |  |  |  | 0