## SUMMERY
CARL JR- LUCKNOW AIRPORT
SUMMARY FOR ELECTRICAL LOAD
REVISION: R0, DATE: 22.01.2024
Sr.No. | DESCRIPTION | WATTAGE (KW) | No of Units | CONNECTED LOAD | MAX. DMD LOAD | DIVERSITY | UPS LOAD
1 | LIGHTING LOAD
a | 600x600mm PANEL LIGHT | 30 | 18 | 0.54 | 0.486 | 90%
b | 1200mm SOFFIT LIGHT | 22 | 7 | 0.154 | 0.1386 | 90%
c | DOWNLIGHT | 18 | 8 | 0.144 | 0.1296 | 90%
d | 1000MM TRACK LIGHT | 5 | 20 | 0.1 | 0.09 | 90%
d | 2000MM TRACK LIGHT | 12 | 6 | 0.072 | 0.0648 | 90%
e | 1400x2100MM SOFFIT LIGHT | 30 | 2 | 0.06 | 0.054 | 90%
f | LED STRIP LIGHT | 22 | 5 | 0.11 | 0.099 | 90%
2 | RAW POWER LOAD
| 6/16A Utlity sockets | 0.1 | 6 | 0.6 | 0.24 | 40%
| USB | 0.01 | 6 | 0.06 | 0.024 | 40%
| POS counters | 0.3 | 2 | 0.6 | 0.48 | 80% | 0.6
| KOT | 0.2 | 2 | 0.4 | 0.4 | 100% | 0.4
| Chilling Machine | 1 | 0 | 0 | 0 | 100% | 0
| Self Service Kiosk | 0.25 | 5 | 1.25 | 1.25 | 100%
| Signage | 1 | 9 | 9 | 9 | 100% | 9
| R.O. Plant | 0.15 | 1 | 0.15 | 0.15 | 100%
| MANAGER TABLE | 0.3 | 1 | 0.3 | 0.3 | 100%
| TV | 0.25 | 5 | 1.25 | 1.25 | 100%
| GAS SUPPRESSION SYETEM | 0.15 | 1 | 0.15 | 0.15 | 100% | 0.15
| FIRE SUPPRESSION SYSTEM | 0.15 | 1 | 0.15 | 0.15 | 100% | 0.15
3 | HVAC LOAD
| AHU | 1.5 | 1 | 1.5 | 1.2 | 80%
0
4 | KITCHEN EQUIPMENTS |  |  | 38.195 | 26.7365 | 70%
5 | FRESH AIR | 2.2 | 1 | 2.2 | 1.76 | 80%
6 | EXHAUST BLOWER | 2.2 | 1 | 2.2 | 1.76 | 80%
.
7 | MISCELLANEOUS |  |  | 2 | 1 | 50%
| TOTAL LOAD IN KW |  |  | 61.185 | 46.9125 |  | 10.3
UPS CALCULATIONS
| Total C & S Load | [5 empty] | 10300
| TOTAL EMERGENCY LOAD 15% of total lighting load | [5 empty] | 0.09
| TOTAL UPS LOAD | [5 empty] | 10300.09
| Load Factor 80% - UPS Load shall be (WATTAGE) | [5 empty] | 8240.072
| After considering 0.85 power factor - VA Rating | [5 empty] | 9694.2024
| Efficiency 80% - UPS Rating shall be (VA) | [5 empty] | 12117.7529
| Recommended UPS rating (KVA) -1PH. I/C & O/G .(with Plus Minus 5%) | [5 empty] | 12.1178
| Nearest size available--(1#10KVA) | [5 empty] | 10
.

## Kitchen BOQ
SR.NO. | DESCRIPTION | OVERALL SIZE | QTY | Make | Model | Vendor | ELECTRICAL |  |  |  | PLUMBING |  |  |  |  | LPG / PNG |  |  | EXHAUST CFM | Tape Model Number | Tape Photo | REMARK
|  | All Dimensions in MM L x W x H |  |  |  |  | HP | Watts | ELECTRICAL LOAD IN KW | PHASE | HOT | COLD | RO | WASTE | Type of Burner | NO OF BURNER | Consumption Per Burner Per Hour | BTU Per Burner Per Hour |  |  |  |  | R | Y | B
1 | Nieco Jet Flow Broiler, JF143-2 Gas Broiler with Incendalyst™ (Catalyst) |  | 1 | Nieco | JF143-2G (for Lucknow) | Middleby Celfrost |  |  | 1 | I | [7 empty] | 35000 |  |  |  |  | 1 |  |  | R5
2 | Neico belt separator |  | 1 | Nieco |  | Middleby Celfrost
3 | Neico Paneer slider |  | 1 | Nieco |  | Middleby Celfrost
4 | Fryer Pitco SGH 50 (set of 2 vat) - Veg Fryer |  | 1 | Pitco | SGH50 | Middleby Celfrost |  |  | 4 | I | [13 empty] | 4 |  | Y2
5 | 12-Channel Timer (Fastron ZAP Z120240) |  | 1 | Fastron | ZAP Z120240 | Middleby Celfrost
6 | 12-Channel Timer (Fastron ZAP Z120240) |  | 1 | Fastron | ZAP Z120240 | Middleby Celfrost
7 | Fryer Pitco SGH 50 (set of 2 vat) - Veg Fryer |  | 1 | Pitco | SGH50 | Middleby Celfrost |  |  | 4 | I | [14 empty] | 4 | B4
8 | Product Holding Unit 4 Width X 2 High (Single Sided) Veg (Prince Castle DHBPT-33GB) | Will be Part of Item Number 34 | 1 | Prince Castle | DHBPT-33GB | Mittal International |  | 2500 | 2.5 | I | [11 empty] | This Will be a Part of item Number 34 | 2.5 |  |  | B3
9 | Product Holding Unit 4 Width X 2 High (Single sided) non-veg (Prince Castle DHBPT-33GB) | Will be Part of Item Number 34 | 1 | Prince Castle | DHBPT-33GB | Mittal International |  | 2500 | 2.5 | I | [14 empty] | 2.5 | R4
10 | Ice Machine & Storage Bin | Kept near in Cold Room | 1 |  |  | Celfrost/ Hoshizaki/ Manitowac/ Scotsman etc. |  |  | 1 | I | [11 empty] | Not Found in Layout |  | 1 |  | Y3
11 | Shake Station ( Drawing Available) | 863 x 750 x 850 | 1 | Gilly | Custom Fabricated |  |  |  | 0.5 | I |  | 12 |  | 100 | [7 empty] | As per Layout legth is 925 |  |  | 0.5 | B6
12 | Shake Blender (Vitamix) |  | 2 | Vitamix | Vitamix Quiet One | Mittal International | [17 empty] | 1 | 0.5 | B8
13 | Spare Number
14 | Spare Number
15 | Single Sink Table | 700 x 750 x 850 + 150 | 1 | Gilly | Custom Fabricated
16 | Undercounter Chiller with s/s top for shake station | 700 x 750 x 850 | 1 | Gilly | Custom Fabricated |  |  |  | 0.5 | I | [11 empty] | As per Layout Length is only 500 |  |  | 0.5 | B5
17 | 2- doors Freezer | 700 x 880 x 2043 | 1 | Blue Star | RF2D700GC |  | .75 HP | 0.56 | 0.56 | I | [11 empty] | As per Layout 600 x 750 | 0.56 |  |  | R1
18 | 2-doors Chiller | 700 x 880 x 2043 | 1 | Blue Star | RC2D700GC |  | .75 HP | 0.56 | 0.56 | I | [11 empty] | As per Layout 600 x 750 |  | 0.56 |  | Y1
19 | s/s breading stn Veg (Gilly) | 932 x 852 x 915 | 1 | Gilly | Custom Fabricated | [16 empty] | Details needed For services |  | 0.4 |  | Y7
20 | s/s breading stn non Veg (Gilly) | 932 x 852 x 915 | 1 | Gilly | Custom Fabricated | [16 empty] | Details needed For services |  | 0.4 |  | Y8
21 | S/S work table | 500 x 750 x 850 + 150 | 1 | Gilly | Custom Fabricated
22 | Chest Freezer (Gilly) |  | 1 | Gilly | Custom Fabricated |  |  |  | 0.5 | I | [13 empty] | 0.5
23 | Walk-In Chiller | 2570 x 2040 x 3000 | 1 | Blue Star |  |  |  |  | 2.5 | III
24 | Walk-in Freezer | 3020 x 2040 x 3000 | 1 | Blue Star |  |  |  |  | 2.5 | III
25 | Water Filtering System | Position In Layout to be determined | 1
26 | Fry Rack with undercounter freezer | 597 x 805 x 1661 | 1 | Gilly | Custom Fabricated |  |  |  | 0.5 | I | [13 empty] | 0.5 |  | Y5
27 | Bun rack with wheel | 700 x 600 x 128 | 3 | Gilly | Custom Fabricated
28 | S/S 3- comp sink | 2056 x 700 x 850 + 150 | 1 | Gilly | Custom Fabricated | [5 empty] | 12 | 12 |  | 100 | [8 empty] | 0.2 |  |  | R8
29 | S/S Prep- sink | 1250 x 600 x 850 + 100 | 1 | Gilly | Custom Fabricated | [5 empty] | 12 | 12 |  | 100 | [8 empty] | 0.2 |  |  | R8
30 | S/s Bun landing table ( No Drawing) | 1400 x 200 x | 1 | Gilly | Custom Fabricated
31 | Prep Table (Metro) | 1200 | 1 | Metro
32 | 3-comp sink wall shelf (Metro) |  | 1 | Metro | [17 empty] | Length is 2844 Where as Sink Length is 2056
33 | Hand free hand wash basin | 346 x 389 x 359 | 2 | Gilly | Custom Fabricated | [16 empty] | As per Layout lenth 255
34 | Shorter Cookline, Single - S/S Main Prep. Counter (Hot Wells) With Top Shelf, Wraping Papers Shelves (Gilly) | 1550 x 750 x 830 + 333 | 2 | Gilly | Custom Fabricated | [16 empty] | As per layout Depth is 700
35 | S/S Pass-Thru Fries Station with Fries Packing Holder | 877 x 851 x 1560 | 1 | Gilly | Custom Fabricated |  |  |  | 3 | I | [12 empty] | 3 |  |  | R6
36 | S/S 2-tier Burger Chute | 1040 x 610 x 815 | 1 | Gilly | Custom Fabricated
37 | S/S transfer table (No Drawing) | 1415 x 1020 x 850 | 1 | Gilly | Custom Fabricated
38 | Walk - in Chiller s/s Thaw Rack (Gilly) | 550 x 685 x 1800 | 2 | Gilly | Custom Fabricated
39 | Walk-in Rack (Cambro) 1848 4T |  | 1 | Cambro | CBSK1848S4580
40 | Walk in chiller rack (Cambro) 1836 4T |  | 2 | Cambro | CBSK1836S4580
41 | Walk -in freezer Bow tie dunnage rack (Cambro) 18x48 |  | 4 | Cambro
42 | Walk-in freezer rack (Cambro) 1860 4T |  | 2 | Cambro | CBSK1860S1580
43 | Coca-Cola 6 or 8-Valves 3/4 Hp Counter Top Post-Mix Dispenser |  | 1 | COKE | [5 empty] | I
44 | Coca-Cola Backroom Package (Carbonator A - Procon Pump) |  | 1
45 | Coca-Cola Backroom Package (Air Compressor Kit, 1/4 hp) |  | 1
46 | Coca-Cola Backroom Package (Water Booster Pump - Procon Pump) |  | 1 | [20 empty] | 0.5 |  | Y9
47 | S/S table for product holding |  | 2 | Gilly | Custom Fabricated
51 | Upright Cooler (Coke) | Only One Found | 2 | [5 empty] | 0.5 | I | [12 empty] | 0.5 |  | 0.5 | B1/R2
52 | Dry Storage Rack (Cambro) - 1848 4T | NOT FOUND IN LAYOUT | 2 | Cambro
53 | Dry Storage Rack (Cambro) - 2448 4T |  | 2 | Cambro
54 | Dry Storage Rack (Cambro) - 1836 4T |  | 1 | Cambro
58 | Fire suppression System 1 Lot (Ansul) |  | 1 | Ansul or Lehavot
Mop Sink
Exhaust Hood
EX-01 | Exhaust Hood With SS Filters | 1220 x 950 x 500 | 1 | CUSTOM FABRICATED
EX-02 | Exhaust Hood With SS Filters | 840 x 900 x 500 | 1 | CUSTOM FABRICATED
EX-03 | Exhaust Hood With SS Filters | 840 x 900 x 500 | 1 | CUSTOM FABRICATED
OTHER ITEM
EXT1 | Water Boiler (Geyser) | 35 Lits. Capacity | 3 |  |  |  |  | 3000 | 3 x 3 | I | [12 empty] | 3 |  | 3 | B2/R3
EXT2 | Air Curtain | BRANDED : 900mm Length | 1 | TECHNOCRAT | SLEEK |  | 1/2 HP | 0.375 | 0.375 | I | [12 empty] | 0.375 |  |  | R7
EXT3 | Insect Killer | BRANDED | 2 | TECHNOCRAT |  |  | 1/2 HP | 0.75 | 0.75 | I | [13 empty] | 1.5 |  | Y6
EXT4 | Garbage Bins |  | 5 | Neelkamal
EXT5 | Exhaust System |  | 1
EXT6 | Fresh - Air System |  | 1
[23 empty] | 11.335 | 10.36 | 11.5
[23 empty] | TOTAL | 33.195
38.195