## EST
PROJECT : LOUNGE , TRIVANDRUM AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
Amount(Rs.)
Part A | Hi Side Works |  |  |  | 0
Part B | DX Unit |  |  |  | 0
PROJECT : LOUNGE , TRIVANDRUM AIRPORT
SUMMARY TO SCHEDULE OF PRICES - HVAC WORKS
The prices are to be quoted in the below mentioned form and shall include the supply, installation, Testing and Commissioning at site of all the equipments, ancillary materials except where specified otherwise and all such items whatsoever which may be required to fulfill the intent and purpose as laid down in the drawings and specifications shall include all taxes and duties on a basis works contract.
S.No. | Description | Unit | Qty. | Rate(Rs.) | Amount(Rs.)
Part A | Hi Side Works
1 | Kitchen Scrubber (Dry Type)-With Fan Section
1.1 | Supply , Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)
The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12.5 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
Power Consumption : Not more than 50W per cell.
Capacities : 3000 CFM
1.2 | DIDW Blower
DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications & Drawings
1.3 | Casing
Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42Kg/Cum with 0.6 mm pre-plasticized /pre-coated Galvanised steel sheet outside & 0.6 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately housed both Electrostatic Modules and Fan with Drive.
1.4 | Accessories
The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt & pulleys, vibration isolators, internal frame works ,canvas connection, Inlet/Outlet flange connection etc
| 5100 CMH (3000 CFM) DIDW Blower Capacity at 80 MM ESP 2.25 KW (3 Phase) motor | Nos | 1 |  | 0
2 | AHU Fan Section
1.1 | Supply, Installation, Testing and Commissioning of Double Skin Type AHU Fan section with 0.6 mm preplasticized/precoated GI sheet outside and 0.6 mm plain Galvanized sheet inside with 25mm injected PUF insulation of 38KG/m3 , G.I. blower section, VFD Operated Plug Fans with motors , base , drive arrangement ,Filter, motor drive suitable for Outdoor Application complete as per specifications and drawings .
1.1.1 | 2500 CFM (with Backward Curve Type DIDW Blowers 1.5 KW Motor ; ESP 30 mm of wg | Nos | 1 |  | 0
3 | Inline Fans (Cabinet Type with acoustic enclosure)
3.1 | 200 CFM at 15 MM ESP | Nos. | 1 |  | 0
| Sub-Total Part-'A' Rs. |  |  |  | 0
Part B | DX UNITS
1 | Air Cooled Split units (Minimum 4-Star rated and latest in present year
1.1 | Supply , Installation , testing and comissioning of Air Cooled Split airconditioners each comprising an outdoor unit consisting of Inverter compressor, air cooled condensing unit, Condenser fan etc. with outer casing and indoor fan coil unit(s) consisting of centrifugal fans, fan motor, DX cooling coil, outer casing, filter, control and power panel with remote control etc. both inter connected with copper refrigerant pipe and drain pipe of required length as given, cabling and wiring, insulation with cross linked polyethelene foam, full charge of refrigerant gas and oil, M.S. base frame, supports etc. complete as per specifications and drawings. The cost shall also include angle iron stands for outdoor units. All ODU's to be placed on Roof Top support system , should be vibration free.
a) | Hi Wall Units (R-32 Refrigerant)
1.1.1 | 1.0 TR Unit (single ref.circuit) | Nos. | 1 |  | 0
b) | Ductable Type (R-32 Refrigerant)
1.1.2 | 5.5 TR Unit (single ref.circuit) | Nos. | 1 |  | 0
1.1.3 | 3.0 TR Unit (single ref.circuit) | Nos. | 1 |  | 0
| Sub-Total Part-'B' Rs. |  |  |  | 0