## HIGH SIDE-CSU UNIT
PROJECT - COPPER CHIMNEY (BANDRA) |  |  |  | Date - 05.06.2024
HIGH SIDE (Ceiling Suspended Unit BOQ)
Sr. No. | Description | Unit | Qty | Rate | Amount | Remarks
Part A | Supply of Air Conditioning Units
1 | Supply of DX Type One Way Cassette Units with Outdoor compressor of following capacity: 2.0 TR (One Way Cassette Unit) - 800CFM |  |  |  |  | Make: Daikin/Bluestar
1.2 | 2.0 TR (One Way Cassette Unit) - 800CFM | Nos | 14 |  | 0
Part A Total
| GST (18%) |  |  |  | 0
| Part A Total including tax |  |  |  | 0

## INSTALL DUCTING & ELE CABLING
PROJECT - COPPER CHIMNEY (BANDRA) |  |  |  | Date - 05.06.2024
LOW STATIC (DUCTING & ELECTRICAL BOQ)
Sr. No. | Description | Unit | Qty | Rate | Amount | Remarks
Part B | Installation of Air Conditioning Units
1 | Installation, Testing & Commissioning of DX Type One Way Cassette Units with Outdoor compressor of following capacity: 2.0 TR (One Way Cassette Unit) - 800CFM
1.1 | 2.0 TR (One Way Cassette Unit) - 800CFM | Nos | 14 |  | 0
2 | Supply, Installation, testing and commissioning of copper refrigerant piping of approved sizes duly insulated with nitrile rubber insulation of 13 mm thickness running inside cable tray. 2.0 TR (One Way Cassette Unit) - 800CFM
2.1 | 2.0 TR (One Way Cassette Unit) - 800CFM | Rmt | 175 |  | 0
3 | SITC of Control Cabling Between Indoor & Outdoor AC unit 4C X 2.5 Sq. mm flexible copper cable
3.1 | 4C X 2.5 Sq. mm flexible copper cable | Rmt | 180
4 | SITC of Power cable between Outdoor unit & Isolator near Outdoor unit 3C X 4 Sq. mm armoured copper cable
4.1 | 3C X 4 Sq. mm armoured copper cable | Rmt | 145
Part C | Installation of Air Conditioning Units
5 | Supply, fabrication, installation and testing of GSS metal ducts as per IS-277 (120 GSM both sides, LFQ & confirming to Class VIII) for GS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers/ supports, volume control duct dampers, accessories, vanes, 3 mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. No slip joints shall be allowed. Flanges shall be Rolamate or equivalent and ducts upto 1500 mm width shall be with rigid support (Gripple support to be provided wherever required) as per technical specifications. 0.63 mm (24 SWG) GSS ducting (601mm-750mm) (TOILET Area)
5.1 | 0.63 mm (24 SWG) GSS ducting (601mm-750mm) (TOILET Area) | Sqmt | 10 |  | 0
6 | Supply & Installation of Gripple wire Support for hanging above duct from supports structure given by client | Lot | 1 |  | 0
7 | EXHAUST AIR INLINE FAN
7.1 | Supply, installation, testing and commissioning INLINE fans are fitted with direct connection two speed motors as standard with thermal over load protection. All motors are suitable for speed control regulation using electronic or auto-transformer.Size from 100 to 315 mm.The adapter enables the MTD fan to be connected to rectangular ducting. (MAKE - KRUGER (MTD Series) a)Circular Inline Fan - 500 CFM, b)Grill Size - 150 x 150mm (Cosmos)
a) | Circular Inline Fan - 500 CFM, | Nos | 1
b) | Grill Size - 150 x 150mm (Cosmos) | Nos | 5
| Part C Total |  |  |  | 0
| GST (18%) |  |  |  | 0
| Part C Total including tax |  |  |  | 0
Note :
Refrigerant gas supply for above DX units is fixed by the vendor