## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
Note: Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | CHILLED WATER TYPE CEILING SUSPENDED AHU (AIR HANDLING UNIT) :
1.1 | CEILING SUSPENDED AHU : Supply and assembly of Ceiling Suspended Double skin cabinet type AHU Integrated (Air handling units) of following specifications: Frame Structure: It shall consist of 48mm Extruded Aluminium with thermal break profile. Panel: 45mm +/- 2mm thick double skin sandwich panels with rockwool insulation of density 64 kg/m3 or PUF insulation of 48 kg/m3 , The sheet thickness shall be minimum 0.6 mm for the outer skin precoated and 0.8 mm thickness for the inner skin of plain GI. Mixing Box: shall be provided wherever specified in the drawing. Filtration Section: It shall be provided with single stage washable type of prefilter 'MERV 8' first stage which shall be placed before coil section. Coil Section: Chilled water coil Multi row deep constructed with Aluminium fins of min 0.11mm thick 12 Fins per inch, and copper tubes of min 27 Guage thickness HYRDOPHYLLIC coated fins. Copper tube shall be min 12.5mm diameter. AHRI certified coil.The coil face area velocity shall not exceed 2.5m/sec (500 fpm). Drain Pan: Condensate drain pan shall be fabricated from 18G SS 304 powder coated, insulated with 13 mm thick closed cell elastomeric(nitrile rubber) insulation. Fan Section: SISW / DIDW Direct drive backward curved fan. The fan section shall be provided with limt switch for safety to shut off fan during Opening of access door. Fan outlet velocity not to exceed 1600 FPM. The sound level shall not be exceed more than 60dB @ 1m from the source. Vibration isolators, Door Limit switch, UV Lamp as per Technical Specifications, AHU Summary Sheet and drawings. Total static pressue has to calculated by Contractor as per the configuration. Other Details : AHU to house control box/ terminal box with Auto-Manual switch and incomer power terminal, with SPP, Over/ Undervoltage protection, shortcircuit protection and with no-nc contacts (potential free contact) to be provided for tripping on signal from Fire Dampers / Fire Alarm Panel. Power cable from Terminal box to motor & control cabling of required size upto the thermostat / sensor etc. to be provided. Internal electrical and control wiring of AHU to be provided as factory fitted from AHU supplier. The cost shall include all necessary supports & accessories required for installation. Contractor shall design the chilled water coil according to the following conditions: a. Coil air entering temperature - 75.4°F DB b. Coil air leaving temperature - 54 deg. F DB/ 52.99 deg. F WB c. Chilled water temperature entering - 7.0 deg. C/ 44.6 deg. F d. Chilled water temperature leaving - 12 deg. C/ 53.6 deg. F Make : VTS / Zeco / Citizen Type Capacity Tonnage ESP No. of (Cfm) TR (mm WG) Rows CS AHU 2000 3.09 25 4/6 | Nos | 1
GENERAL NOTES: a. LHS & RHS VALVE station location to be confirmed. b. Fan outlet velocity - 1600 FPM c. Contractor shall submit static pressure calculation for all above units to Client/Consultant. d. Any change in motor HP shall be made at no extra cost to client. f. Fan efficiency shall be minimum 75% g. The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
3 | VENTILATION SYSTEM KITCHEN EXHAUST FANSITC of KITCHEN EXHAUST FANS. Fan shall be circular mixed flow / cabinet with belt driven centrifugal fan / plug type fan. Fan and cabinet for Kitchen exhaust fans shall be suitable for smoke exhaust application and thermally rated for 250°C for 2 hours as per [BS EN 12101-3: 2002] Class-B. Motor and belt drive shall be mounted outside, so that it is not exposed to smoke stream. Motors shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply, VFD drive compatible. Fan static pressure shall be as indicated. Fans shall be activated from fire signal from fire alarm system. Fan shall be with fire proof flexible connection at inlet and outlet. The minimum fan efficiency shall be 75%. The fan shall have low sound level exceeding not more than 65 DBA at 1.5 meter distance. The speed of the fans shall not exceed 1440 RPM for fans. Baseframe, canvass connections, ancillary structure required to suspended from slab/beams, vibration isolators, vibration pads, connection flanges, inlet bell mouth/inlet cone, outlet cone, back draft dampers, volume control and fire damper. (Vendor to crosscheck static pressure calculation) Make : Greeheck, Nicotra, Waves, EdgeTech, Kruger, Wolter, Caryaire
a | 4800 CFM, 60mm ESP (Class H) | Nos. | 1
3.2 | DRY SCRUBBER Supply, Installation, Testing and Commissioning of DRY SCRUBBER each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the specifications and as under:CE Certified (Produce valid CE Certification) Electrostatic Filter manufactured with 16G MS powder coated cabinet complete with washable type aluminium mesh filters, tungsten wire/ stainless steel spiked ionizers to create high voltage DC field, aluminium collector plates which should be alternatively charged positive and negative with large collecting area (Minimum filtration area of 2.00sqm per 1000 CMH) with minimum 13.5" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method (ASHRAE standard 52.2-2012 Produce valid test report) Electrostatic precipitator should be able to charge particles from 0.01micron to 10micron through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. All the units shall be equipped with pulse width modulating (PWM) power circuit board. The system should be fitted with interlock switch for safety. The unit must have potential Free NO contact for monitoring thru BMS system and set of terminals for remote monitoring thru LED Indicators. The units should be supplied with Auto Wash and V shaped Adsorber Module as per specifications, if specifically asked for in BOQ. All the systems must be suitable for OUTDOOR Installation.Operating Voltage: 220V, 50HzIonizing Voltage: 12.5 to 13KVDCCollector Cell Voltage: 6 to 6.5KVDCPower Consumption: Not more than 50W per cellDry scrubber shall be supplied with factory fitted UVO3 system, with ozone generating UVC lamps, interlocked with scrubber operation. The lamps must be fitted post the ESP on stand easily accessible from the scrubber door for maintenance/ replacement. The lamps must be supplied with Electronic Ballasts, mounted suitably within the scrubber control panel and completely interlocked. Lamp operation LED indicators must be available on the panel. Lamp life shall be minimum 13000hr.Make : Rydair, Trion, Espair, Halton
a | 4800 CFM | Nos. | 1
3.3 | KITCHEN FRESH AIR FANSITC of KITCHEN FRESH FANS. Fan shall be circular mixed flow / cabinet with belt driven centrifugal fan / plug type fan. Fan and cabinet for Kitchen fresh air fans shall be suitable for smoke exhaust application and thermally rated for 250°C for 2 hours as per [BS EN 12101-3: 2002] Class-B. Motor and belt drive shall be mounted outside, so that it is not exposed to smoke stream. Motors shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply, VFD drive compatible. Fan static pressure shall be as indicated. Fans shall be activated from fire signal from fire alarm system. Fan shall be with fire proof flexible connection at inlet and outlet. The minimum fan efficiency shall be 75%. The fan shall have low sound level exceeding not more than 65 DBA at 1.5 meter distance. The speed of the fans shall not exceed 1440 RPM for fans. Baseframe, canvass connections, ancillary structure required to suspended from slab/beams, vibration isolators, vibration pads, connection flanges, inlet bell mouth/inlet cone, outlet cone, back draft dampers, volume control and fire damper. In additional all fresh air fans shall be provided with prefilter (MERV 8) and fine filter (MERV 13). Make : Greeheck, Nicotra, Waves, EdgeTech, Kruger, Wolter, Caryaire
a | 4100 CFM, 30mm ESP (Class F) | Nos. | 1