## SUMMARY
SWAMI SNACKS BAR @ T1 TRV
VENTILATION BOQ SUMMARY
Sr.No | Description | Total Amount
1 | VENTILATION SYSTEM | 0
2 | SHEET METAL WORKS - | 0
#REF! | #REF! | #REF!
4 | ELECTRICAL WORKS - | 0
| SUB - TOTAL WITHOUT TAX | #REF!
CGST @ 9%
SGST @ 9%
Other taxes if applicable
TOTAL WITH TAX

## HVAC
SWAMI SNACKS BAR @ T1 TRV
VENTILATION BOQ
Sr. No. | Description Items | Unit | Qty | Supply Rate | Installation Rate | Total Amount
Sr.No. | Item Description
Note - | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | VENTILATION SYSTEM
1.5 | FRAMEWORK FOR FANS
| Supply, Fabrication and Installation of MS frame using channels OR angle iron sections as required for mounting of ventilation fans & scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects OR Structural Engineers prior to commencement of fabrication. | Kg | 100 | 0 | 0 | 0
Note -
a. | Fan outlet velocity - 1600 FPM
b. | All cabinet fans should have plenum section.
c. | Fresh air fan should to have 6mm thick synthetic media washable filter with framework.
d. | Contractor shall submit static pressure calculation for all above units to Client OR Consultant for their approval. Also, the total static drops across the systems shall cover the overall length from suction OR discharge to grille (inside the outlet).
e. | Any change in motor HP or coil selection shall be made at no extra cost to client.
f. | Fan efficiency shall be minimum 75%
g. | The cost shall be included liftting & shifting of each equipment OR material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material OR equipment.
| SUB-TOTAL |  |  |  |  | 0
2 | SHEET METAL WORKS -
2.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA and IS 655 standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes - Tata, Jindal, SAIL, Ispat
Make - Rola Star, Zeco & Ductofab
d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 15 |  |  | 0
2.6 | MULTI LEAF VOLUME CONTROL DAMPER
| SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 0.5 |  |  | 0
Make - Cosmos, Air Master & System Air
2.8 | CANVAS CONNECTION
SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
a | For Ventilation Fan | Nos | 2 |  |  | 0
NOTES -
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW OR SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
| SUB-TOTAL |  |  |  |  | 0
4 | ELECTRICAL WORKS -
4.1 | STARTER PANEL
SITC of indoor OR outdoor, wall mounting type DOL OR Delta 3PH, 415V AC MOTOR STARTERS with VFD in CRCA Sheet Steel enclosure with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP & BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB OR MCCB, Contactor, Bi-metal O OR L relay with SPP, ON OR OFF Push buttons, on OR off OR trip indication Lamp, on off push button, & phase indication Lamp. Selection of relay, contractor, MPCB OR MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure.
| Suitable for DOL STARTER |  |  |  |  | 0
a | 950 CFM Exhaust fan without VFD | Nos. | 1
4.2 | ISOLATOR
| S & I of 16A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc (FOR EXHAUST & FRESH AIR FAN) | Nos. | 1 | 0 | 0
4.3 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium OR Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners OR Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB S be provided near each Fan OR ODU by electrical contractor.
Suitable Power Cable -
a | 950 CFM Exhaust fan without VFD | Rmt | 5 |  |  | 0
b | 950 CFM Dry Scrubber | Rmt | 5 |  |  | 0
e | Earthing -
| 8 SWG GI Earthing | Rmt | 10 |  |  | 0
4.4 | CABLE TERMINATION -
Supply & Making of Cable termination of armoured OR unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
Suitable for
a | 950 CFM Exhaust fan without VFD | Nos. | 2 | 0 | 0 | 0
4.5 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall OR suspended from the ceiling with necessary MS supports.
a | 50mm wide x 1.6mm thick | Rmt | 5 | 0 | 0 | 0
| SUB-TOTAL |  |  |  |  | 0
| GRAND TOTAL |  |  |  |  | #VALUE!