## SUMMARY
MALABAR TIFFINS @ T2 TRV
VENTILATION BOQ SUMMARY
Sr.No | Description | Total Amount
1 | VENTILATION SYSTEM | 0
2 | SHEET METAL WORKS: | 0
3 | THERMAL & ACOUSTIC INSULATION: | 0
4 | ELECTRICAL WORKS: | 0
| SUB - TOTAL WITHOUT TAX | 0
CGST @ 9%
SGST @ 9%
Other taxes if applicable
TOTAL WITH TAX

## HVAC
MALABAR TIFFINS @ T2 TRV
VENTILATION BOQ
Sr. No. | Description Items | Unit | Qty | Supply Rate | Installation Rate | Total Amount
Sr.No. | Item Description
Note: | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | VENTILATION SYSTEM
1.5 | FRAMEWORK FOR FANS
| Supply, Fabrication and Installation of MS frame using channels/angle iron sections as required for mounting of ventilation fans & scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects/ Structural Engineers prior to commencement of fabrication. | Kg | 250 | 0 | 0 | 0
Note:
a. | Fan outlet velocity - 1600 FPM
b. | All cabinet fans should have plenum section.
c. | Fresh air fan should to have 6mm thick synthetic media washable filter with framework.
d. | Contractor shall submit static pressure calculation for all above units to Client/Consultant for their approval. Also, the total static drops across the systems shall cover the overall length from suction / discharge to grille (inside the outlet).
e. | Any change in motor HP or coil selection shall be made at no extra cost to client.
f. | Fan efficiency shall be minimum 75%
g. | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.
| SUB-TOTAL |  |  |  |  | 0
2 | SHEET METAL WORKS:
2.1 | FACTORY FABRICATED G.I RECTANGULAR DUCT
Supply, Fabrication, Testing, and Commissioning of Factory Fabricated GI Sheet Metal 120GSM Rectangular boxed ducting, Plenums, Cowls, Elbows with turning vanes, Splitters, Reducers, Flanges, Collars etc as per IS and Installaton as per SMACNA and IS 655 standards, The complete ducting shall be provided with MS Supports, Rods, Angles, Flanges, Bracing, Rubber Gaskets, Wooden frames, Canvas Connections, etc. as per drawings and specifications.
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
a | 18 Gauge GI Sheet Metal Duct (Above 2251mm & Plenum) | Sq.mtr | 10
c | 22 Gauge GI Sheet Metal Duct (751-1500mm) | Sq.mtr | 5 |  |  | 0
d | 24 Gauge GI Sheet Metal Duct (0-750mm) | Sq.mtr | 100 |  |  | 0
2.2 | SS EXHAUST AND FRESH AIR GRILLES
SITC of 18G S.S 304 Grills adjustable Double Deflector With S.S Volume Control Dampers. Grills to be of Double Deflection Type for ease of deflection on all sides and to have necessary built in Dampers for adjustable nature.
Make: Carryaire / System Air / Dynacraft / Air Master
a | Linear / Square / Rectangular Grille | Sq.mtr | 0.5 |  |  | 0
2.3 | EXTRUDED ALUMINIUM LOUVER with BIRD SCREEN
| SITC of Aluminium extruded powder coated Louver with four side flanges, wire mesh bird screen etc. | Sq.mtr | 0.5
2.4 | OPPOSED BLADE DAMPER
| SITC of Aluminium Opposed blade dampers black powder coated vertical blades type for supply air collar. The damper should be gear operated type. | Sq.mtr | 0.5 |  |  | 0
Make: Cosmos, Air Master & System Air
2.6 | MULTI LEAF VOLUME CONTROL DAMPER
| SITC of opposed blade aerofoil type 1.2 mm thick Anodized Aluminium volume control dampers for ducts shall be provided with concealed gears, plastic operator and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sq.mtr | 1.5 |  |  | 0
Make: Cosmos, Air Master & System Air
2.7 | CURTAIN TYPE FIRE DAMPER
SITC of curtain type fire dampers consist of 16G GI frame, 20G GI interlocking blades secured with SS springs, blades outside airstream clamped with fusible link UL-555 listed with melting point 165 / 225°F, etc; as per the approved shop drawings and specifications.
Make: Cosmos, Air Master & System Air
a | Bare fire dampers | Sq.mtr | 0.5
b | Fusible link as per specification UL 555 and CBRI approved | Nos. | 1
2.8 | CANVAS CONNECTION
SITC of Flexible connections between mouth piece of Fan and initial piece of ducting with inspection zip. Flexible connections shall be double thickness non-flammable material (Fire retardant type).
a | For Ventilation Fan | Nos | 3 |  |  | 0
NOTES:
The ducting support should be as per tender specification and additional supports are to be provided by Contractor as decided by Consultant.
Muslin cloth cover for all air outlets during construction.
Pressure testing of complete duct work as per DW/ SMACNA standard.
Silicon sealant for longitudinal & transverse joints as per specification.
Diffusers & grilles shall be powder coated as per color approved by Architect.
| SUB-TOTAL |  |  |  |  | 0
3 | THERMAL & ACOUSTIC INSULATION:
3.1 | THERMAL INSULATION FOR KITCHEN EXHAUST DUCTS
SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade.
Makes : UP Twiga, Owens Corning, Supreme
| 25 mm Thick | Sq.mtr | 120
Note:
a. | Insulation work to be coordinated with other agencies and repair to be included by contractor as per site requirement.
b. | Vendors to take care of the installation, if any damages takes place the vendor to repair or replace and hand over to clients in good and acceptable condition.
c. | Thermal insulation shall be internal for Elliptical / Expossed ducting.
| SUB-TOTAL |  |  |  |  | 0
4 | ELECTRICAL WORKS:
4.1 | STARTER PANEL
SITC of indoor / outdoor, wall mounting type DOL / Delta 3PH, 415V AC MOTOR STARTERS with VFD in CRCA Sheet Steel enclosure with necssary supporting brackets and required accessories, etc., The Enclosure shall be provided with knockouts suitable for cable termination at TOP & BOTTOM for incoming and outgoing power cables of A2XFY type and size specified. The starters shall be complete with suitable MPCB/MCCB, Contactor, Bi-metal O/L relay with SPP, ON/OFF Push buttons, on / off / trip indication Lamp, on off push button, & phase indication Lamp. Selection of relay, contractor, MPCB/MCCB etc. as per Type-2 Coordination. Starter panel shall be BMS compatible. Variable frequency drives shall be provided with necessary sensors and controllers complete with control wiring in all respect as required. VFDs shall be provided with necessary bypass arrangement inside electrical starter panels with IP-55 enclosure.
| Suitable for DOL STARTER |  |  |  |  | 0
a | 5200 CFM Exhaust fan without VFD | Nos. | 1
b | 4400 CFM Fresh Air Fan without VFD | Nos. | 1
4.2 | ISOLATOR
| S & I of 25A, FP, 300mA ELMCB, in powder coated (IP66) sheet metal box for terminating power to equipment etc (FOR EXHAUST & FRESH AIR FAN) | Nos. | 2 | 0 | 0
4.3 | POWER CABLING
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium /Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB S be provided near each Fan / ODU by electrical contractor.
Suitable Power Cable:
a | 5200 CFM Exhaust fan without VFD | Rmt | 20 |  |  | 0
b | 4400 CFM Fresh Air Fan without VFD | Rmt | 20 |  |  | 0
c | 5200 CFM Dry Scrubber | Rmt | 10 |  |  | 0
e | Earthing:
| 8 SWG GI Earthing | Rmt | 80 |  |  | 0
4.4 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
Suitable for
a | 5200 CFM Exhaust fan without VFD | Nos. | 2 | 0 | 0 | 0
b | 4400 CFM Fresh Air Fan without VFD | Nos. | 2 | 0 | 0 | 0
4.5 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm wide x 1.6mm thick | Rmt | 40 | 0 | 0 | 0
| SUB-TOTAL |  |  |  |  | 0
| GRAND TOTAL |  |  |  |  | 0