## SUMMARY
MALABAR TIFFINS @ T1 TRV
VENTILATION BOQ SUMMARY
Sr.No | Description | Total Amount
1 | VENTILATION SYSTEM | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| SUB - TOTAL WITHOUT TAX | #REF!
CGST @ 9%
SGST @ 9%
Other taxes if applicable
TOTAL WITH TAX

## HVAC
MALABAR TIFFINS @ T1 TRV
VENTILATION BOQ
Sr. No. | Description Items | Unit | Qty | Supply Rate | Installation Rate | Total Amount
Sr.No. | Item Description
Note: | Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | VENTILATION SYSTEM
1.1 | KITCHEN EXHAUST AIR FAN
SITC of Cabinet type SISW Centrifugal Blower, Direct Drive, Statically & Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 65 rating with Class H Insulation motor, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame and required accessories. (Vendor to crosscheck static pressure calculation).
Make :Waves / Systems Air / Nicotra / Humidin
a | 4450CFM, 60mm TSP | No. | 1 |  |  | 0
1.2 | KITCHEN DRY SCRUBBER
SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% & units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
Finishing - Power coated, Dark Blue
Operating voltage - 220 Vac+/-10%, 50 Hz (Single phase)
Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
Particle Size - Collects particles as small as 0.01 microns
Motor - Sealead ball bearings UL, single phase.
Cell - Ionizing voltage - 12 KVdc
Collector voltage - 6 KVdc
One cell comprising of 9 ionizing wires and 25 collection plates
Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
Pre-filter - Aluminium mesh, washable Dry contact for BMS.
Make: Rydair / Espair
| CFM - 4550 | Nos. | 1 | 0 | 0 | 0
1.4 | CABINET FRESH AIR FAN
SITC of Cabinet type Fresh Air fan with Centrifugal Blower, Belt / Direct Drive, Statically & Dynamically Balanced, Backward Curved Impeller, Speed regulator, Dunlop Anti- Vibration Pads, etc. Motor should be TEFC squirrel cage, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 65dB @ 3mtr distance. MERV 8 / G4 pleated pre-filters should be made of 100% synthetic media to capture common airborne contaminants as per ASHRAE Standard 52.2. Fan shall be BMS compatible. Power will be provided 5 ft away from fan and necessary control wiring with plug will be provided by AC contractor.(Vendor to crosscheck static pressure calculation)
Make :Waves / Systems Air / Nicotra / Humidin
a | FRESH AIR FAN WITH MERV 8
| 2100 CFM, 30mm TSP | Nos | 1