## High side HVAC BOQ
NAME OF PROJECT: Air side Central Kitchen at Hyderabad
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE |  | AMOUNT
|  |  |  | Supply | Installation | Supply | Installation
1 | Air cooled VRV Unit
Supply, installation, testing & Comissioning of Modulating outdoor units,with scroll compressors with capacity controlling compressor, specialpre-coated fins, panel, corrosion resistant & hydrophillic treatment coated condenser, variable speed based condenser fan, electrical & microprocessor panel, isolating valves, factory gas charged (R-407 or R-410 a) and all the necessary accessories for proper functioning of the units, having following approximate capacities. The unit shall also have heating provision during winter season. Capacity as listed below.
The Unit shall deliver the rated capacity at AHRI Conditions and work even at 50 Deg C ambient temperature without tripping.. The unit capacities shall be after taking deration into account due to copper piping lengths:
All the machines shall be selected with minimum COP of 3.7 (at 100% Load) at AHRI conditions (35deg C Outdoor Conditions).
VRF based outdoor unit machines as described above.
Supply of imported portion of above VRF based outdoor unit at Site
Indicate for all VRF based outdoor unit port charges, port handling charges, other local duties, loading, transportation / insurance upto site, octroi charges and all other taxes & incidentals complete till delivered at site.
Custom duty and counterveiling duty against licence for the above imported equipments.
Note: Painted M.S. angle stand (With one coat of primer and two coats of enamel paint) for outdoor unit & Rubber base must be included in the cost.
1.1 | 8 HP | Nos. | 1
2 | VRV Indoor units
Supply, installation, testing & comissioning of VRF based indoor units complete with LCD display Corded remote controller having following approximate capacities. Quoted price shall include the price of factory fitted drain pump.
Sound level of VRF based Indoor Unit shall not exceeding 45 dB (A)
Total static pressure of VRF based indoor unit shall be as per the site requirement & same shall be checked by Vendor, accordingly unit model to be provided.
Supply imported portion of above VRF based indoor units at CIF nearest port and transportation of the same to site
Indicate for all VRF based indoor unit port charges, port handling charges, other local duties, loading, transportation / insurance upto site, octroi charges and all other taxes & incidentals complete till delivered at site.
Custom duty and counterveiling duty against licence for the above imported equipments.
Ceiling concealed ductable type having following approximate capacities.
2.1 | 1.3 TR ± 5% ( 565 CFM) | No. | 1
2.2 | 2.6 TR ± 5% ( 883 CFM) | No. | 1
Hi-wall unit type having following approximate capacities.
2.3 | 0.65 TR ± 5% (265 CFM) | No. | 2
GRAND TOTAL

## Low side HVAC BOQ
NAME OF PROJECT: Air side Central Kitchen at Hyderabad
HVAC WORK
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 24G sheet | sq.m | 70
| 26G sheet | sq.m | 5
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 10
3 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 1
4 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1
5 | Supply, installation, testing and balancing of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 1
6 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 2
7 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape supply air diffusers with removable core & anti smudge ring & volume control dampers as per approved drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 1.5
8 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction. Square / round shape return air diffusers with removable core, antismudge ring & without volume control damper as per specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 1.5
9 | Supply, installation and testing of Acoustic lining with Open cell nitrile rubber with in supply and return air ducts of specified thickness as per the specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as perthe specifications:
| 15 mm thick | sq.m | 10
10 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber(Class“O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
| 19mm thick | sq.m | 80
11 | Supply, installation, Testing & Commissioning of Imported Control Systems & Y-Joints :
11.1 | Supply , Installation, testing and commissioning of Imported fittings Y-joints & associated refrigerant header connections & refrigerant branching kit for proper & efficeint functioning of the system. | Set | 3
11.2 | Corded remote compatible with BMS | Nos. | 2
11.3 | Cordless remote compatible with BMS | Nos. | 2
12 | Providing & fixing of inter connecting copper piping between indoor & outdoor units as per manufacturer specifications duly insulated with closed cell nitrile foam tabular insulation of 13/19mm thickness. All piping inside the room shall be properly supported with hanger in M.S. painted cable tray .
| 6.4 mm OD soft copper (Insulation 13 mm) | RM | 15
| 9.5 mm OD soft copper (Insulation 13 mm) | RM | 40
| 12.7 mm OD soft copper (Insulation 13 mm) | RM | 15
| 15.9 mm OD soft copper (Insulation 19 mm) | RM | 15
| 19.1 mm OD hard copper (Insulation 19 mm) | RM | 30
| 22.2 mm OD hard copper (Insulation 19 mm) | RM | 1
13 | Fabricating and installing following size of perforated G.I cable trays to run the insulated refreigerant pipes (directly exposed to ambient) & electrical power & control cables (directly exposed to ambient) including horizontal and vertical bends, reducers, tees, cross members & other accessories as required and duly supported from the floor as required.
13.1 | 100 mm width X 50 mm depth X 2 mm thickness | RM | 20
14 | Supplying, installing and testing of UPVC pipe ( heavy duty) with 6 mm thick nitrile rubber insulation with protective coating on condensing water piping and fitting like bends, elbow, tee and union, etc. as per the approved shop drawings and specifications.
| 32 mm dia | RM | 5
| 25 mm dia | RM | 20
15 | Supply, laying, testing and commissioning of PVC sheathed stranded FRLS wires in MS conduits recessed / surface including cutting, chesing the wall surface and making for the same, sizes as given below of copper conductor including terminations complete as required.
15.1 | 2C x 1.5 mm2 (control wiring for IDU to ODU) | RM | 60
16 | Supply & installation, testing and commissioning of following sizes of copper strip/wire clamped to walls, cable trays or on surface etc for equipment earthing complete as required including inter connection between length at joints, all fixing accessories, saddles, clamps and other fixing hardware material as required for proper installation.
| 8 SWG GI Wire | RM | 10
17 | Supply, installation, testing and commissioning of air curtain of 2 Meter width having air throw velocity of 16 to 21 m/sec, with dual speed, Al chassis with CRC Plates, low noise level up to 56 to 59 dB suitable for door height upto 9 feet, working on 1ph, 230 V, 50Hz, A.C. supply. | Nos. | 1
GRAND TOTAL

## MAKE LIST
NAME OF PROJECT: Air side Central Kitchen at Hyderabad
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
9 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
10 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
11 | Cables | Polycab / Finolex / Hawells
12 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
13 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
14 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
15 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
16 | Air curtain | Mitzvah / Mitsubishi / Olefini
17 | VRF / VRV unit | Toshiba / Bluestar / Daikin / Samsung / Mitsubishi/LG/Hitachi /Voltas
18 | UPVC Drain Piping | Prince / Supreme
19 | Copper Pipes | Maxflow / Yorkshire / Rajco / Mehta tubes
20 | Copper Pipe fittings | Conex Banninger/ NIBCO
21 | Copper Pipe Insulation | Thermobreak / Supreme