## Load
PROPOSED ELECTRICAL LOAD LIST FOR BAR SUPPORT KITCHEN NOIDA INTERNATIONAL AIRPORT | [8 empty] | DATE | 13.11.2024
SR.NO. |  | APPLIANCE | VOLTS | WATTS | NOS | TOTAL CONNECT LOAD WATTS | TOTAL CONNECT LOAD KW | D/F | MD WATTS | TOTAL MD LOAD KW | TOTAL UPS LOAD WATTS
1 | SB NO | KITCHEN
1.1 | SB-01 | HOOD LIGHT | 220 | 250 | 1 | 250 | 0.25 | 0.8 | 200 | 0.2
1.2 | SB-02 | COMBI OVEN | 415 | 9300 | 1 | 9300 | 9.3 | 0.8 | 7440 | 7.44
1.3 | SB-03 | DEEP FAT FRYER | 415 | 16500 | 1 | 16500 | 16.5 | 0.8 | 13200 | 13.2
1.4 | SB-04 | DEEP FAT FRYER | 415 | 16500 | 1 | 16500 | 16.5 | 0.8 | 13200 | 13.2
1.5 | SB-05 | HOOD LIGHT | 220 | 250 | 1 | 250 | 0.25 | 0.8 | 200 | 0.2
1.7 | SB-06 | HOOD LIGHT | 220 | 250 | 1 | 250 | 0.25 | 0.8 | 200 | 0.2
1.8 | SB-07 | REFRRIGERATOR | 220 | 375 | 2 | 750 | 0.75 | 0.8 | 600 | 0.6
1.9 |  | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.1 | SB-08 | CHILLER | 220 | 750 | 1 | 750 | 0.75 | 0.8 | 600 | 0.6
1.11 |  | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.1 | SB-09 | BAIN MARIE | 220 | 4000 | 1 | 4000 | 4 | 0.8 | 3200 | 3.2
1.2 | SB-10 | SPARE | 220 | 500 | 1 | 500 | 0.5 | 0.8 | 400 | 0.4
1.3 | SB-11 | INDUCTION TOP | 220 | 3500 | 1 | 3500 | 3.5 | 0.8 | 2800 | 2.8
1.4 | SB-12 | INDUCTION TOP | 220 | 3500 | 1 | 3500 | 3.5 | 0.8 | 2800 | 2.8
1.5 | SB-13 | PEST O FLASH | 220 | 500 | 1 | 500 | 0.5 | 0.8 | 400 | 0.4
1.7 | SB-14 | 2 DOOR VERTICAL CHILLER | 220 | 250 | 1 | 250 | 0.25 | 0.8 | 200 | 0.2
1.8 | SB-15 | 2 DOOR VERTICAL FREEZER | 220 | 522 | 1 | 522 | 0.522 | 0.8 | 417.6 | 0.4176
1.9 | SB-16 | GEYSER | 220 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
2 |  | OTHERS
2.1 |  | Exhaust Air Fan (8520 CFM) | 415 | 7500 | 1 | 7500 | 7.5 | 0.8 | 6000 | 6
2.2 |  | Fresh Air Fan (6800 CFM) | 415 | 5500 | 1 | 5500 | 5.5 | 0.8 | 4400 | 4.4
2.3 |  | Dry Scrubber | 220 | 250 | 1 | 250 | 0.25 | 0.8 | 200 | 0.2
|  | UPS 2KVA | 220 | 1500 | 1 | 1500 | 1.5 | 0.8 | 1200 | 1.2
2.4 |  | Lighting | 220 | 1500 | 1 | 1500 | 1.5 | 0.8 | 1200 | 1.2
[6 empty] | 77572 | 77.572 |  | 62057.6 | 62.0576
LOAD CALULATIONS
[6 empty] | 0.8 | PF
TOTAL CONNECTED LOAD |  |  |  | 77.572 | KW | 96.965 | KVA
MAX. DEMAND LOAD |  |  |  | 62.0576 | KW | 77.572 | KVA
AVERAGE LOAD FACTOR |  |  |  | 0.9 | KW
FINAL DEMAND LOAD |  |  |  | 55.8518 | KW | 69.8148 | KVA
CURRENT CALCULATIONS
FINAL DEMAND LOAD |  |  |  | 55.8518 | KW
POWER FACTOR |  |  |  | 0.85
CURRENT |  |  |  | 91.4161 | AMP
MAIN SWITCH RATING FACTOR |  |  |  | 1.25
MAIN SWITCH RATING |  |  |  | 114.2701 | AMP
SUGGESTED MAIN SWITCH |  |  |  | 200 | AMP
CABLE CALCULATIONS
CURRENT |  |  |  | 91.4161 | AMP
CABLE LAYING METHOD : IN GROUND
FACTOR FOR IN GROUND LAYING |  |  |  | 0.7
DESIGN CURRENT |  |  |  | 130.5944 | AMP
35 MM2 ALU / XLPE CABLE CURRENT IN GND |  |  |  | 117 | AMP
NUMBER OF RUNS |  |  |  | 1.1162
CABLE SIZE & NUMBER OF RUNS [ALU] |  |  |  | 2 | RUNSx 35MM2
POWER FACTOR CONTROL CALCULATIONS
FINAL DEMAND LOAD |  |  |  | 55.8518 | KW
UNCORRECTED POWER FACTOR |  |  |  | 0.85
CORRECTED POWER FACTOR |  |  |  | 0.98
FACTOR FOR CORRECTION |  |  |  | 0.417
KVAR REQUIRED |  |  |  | 23.2902 | Kvar
SUGGESTED DESIGNED KVAR |  |  |  | 30 | Kvar
TOTAL AMP = 140AMP
REQUIRED BREAKER = 150 AMP
CABLE SIZE FOR 150 AMP = 70 Sqmm