## Load
PROPOSED ELECTRICAL LOAD LIST FOR BASE KITCHEN NOIDA INTERNATIONAL AIRPORT | [8 empty] | DATE | 15.11.2024
SR.NO. |  | APPLIANCE | VOLTS | WATTS | NOS | TOTAL CONNECT LOAD WATTS | TOTAL CONNECT LOAD KW | D/F | MD WATTS | TOTAL MD LOAD KW | TOTAL UPS LOAD WATTS
1 | SB | KITCHEN
1.1 | SB-01 | GEYSER | 220 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.2 | SB-02 | PEST O FLASH | 220 | 500 | 1 | 500 | 0.5 | 0.8 | 400 | 0.4
1.3 | SB-03 | GEYSER | 220 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.4 | SB-04 | PEST O FLASH | 220 | 500 | 1 | 500 | 0.5 | 0.8 | 400 | 0.4
1.5 | SB-05 | GEYSER | 220 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.6 | SB-06 | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.7 | SB-07 | REFRIGERATOR | 220 | 730 | 1 | 730 | 0.73 | 0.8 | 584 | 0.584
1.8 |  | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.9 | SB-08 | REFRIGERATOR | 220 | 730 | 1 | 730 | 0.73 | 0.8 | 584 | 0.584
1.1 |  | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.11 | SB-09 | DEEP FAT FRYER | 415 | 16500 | 1 | 16500 | 16.5 | 0.8 | 13200 | 13.2
1.12 | SB-10 | DEEP FAT FRYER | 415 | 16500 | 1 | 16500 | 16.5 | 0.8 | 13200 | 13.2
1.13 | SB-11 | COMBI OVEN | 415 | 10800 | 1 | 10800 | 10.8 | 0.8 | 8640 | 8.64
1.14 | SB-12 | COMBI OVEN | 415 | 10800 | 1 | 10800 | 10.8 | 0.8 | 8640 | 8.64
1.15 | SB-13 | GEYSER | 220 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.16 | SB-14 | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.17 | SB-15 | PEST O FLASH | 220 | 500 | 1 | 500 | 0.5 | 0.8 | 400 | 0.4
1.18 |  | SPARE | 220 | 250 | 2 | 500 | 0.5 | 0.8 | 400 | 0.4
1.19 | SB-16 | WALK IN FREEZER | 415 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.2 | SB-17 | WALK IN COOLER | 415 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.21 | SB-18 | WALK IN COOLER | 415 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
1.22 | SB-19 | WALK IN FREEZER | 415 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
2 |  | OTHERS
2.1 |  | Exhaust Air Fan (6800 CFM) | 415 | 5500 | 1 | 5500 | 5.5 | 0.8 | 4400 | 4.4
2.2 |  | Fresh Air Fan (5440 CFM) | 415 | 4500 | 1 | 4500 | 4.5 | 0.8 | 3600 | 3.6
2.3 |  | Dry Scrubber | 220 | 250 | 1 | 250 | 0.25 | 0.8 | 200 | 0.2
2.4 |  | UPS 2KVA | 415 | 1500 | 1 | 1500 | 1.5 | 0.8 | 1200 | 1.2
2.5 |  | Lighting | 220 | 3000 | 1 | 3000 | 3 | 0.8 | 2400 | 2.4
[6 empty] | 98810 | 98.81 |  | 79048 | 79.048
LOAD CALULATIONS
[6 empty] | 0.8 | PF
TOTAL CONNECTED LOAD |  |  |  | 98.81 | KW | 123.5125 | KVA
MAX. DEMAND LOAD |  |  |  | 79.048 | KW | 98.81 | KVA
AVERAGE LOAD FACTOR |  |  |  | 0.9 | KW
FINAL DEMAND LOAD |  |  |  | 71.1432 | KW | 88.929 | KVA
CURRENT CALCULATIONS
FINAL DEMAND LOAD |  |  |  | 71.1432 | KW
POWER FACTOR |  |  |  | 0.85
CURRENT |  |  |  | 116.4444 | AMP
MAIN SWITCH RATING FACTOR |  |  |  | 1.25
MAIN SWITCH RATING |  |  |  | 145.5555 | AMP
SUGGESTED MAIN SWITCH |  |  |  | 200 | AMP
CABLE CALCULATIONS
CURRENT |  |  |  | 116.4444 | AMP
CABLE LAYING METHOD : IN GROUND
FACTOR FOR IN GROUND LAYING |  |  |  | 0.7
DESIGN CURRENT |  |  |  | 166.3491 | AMP
35 MM2 ALU / XLPE CABLE CURRENT IN GND |  |  |  | 117 | AMP
NUMBER OF RUNS |  |  |  | 1.4218
CABLE SIZE & NUMBER OF RUNS [ALU] |  |  |  | 2 | RUNSx 35MM2
POWER FACTOR CONTROL CALCULATIONS
FINAL DEMAND LOAD |  |  |  | 71.1432 | KW
UNCORRECTED POWER FACTOR |  |  |  | 0.85
CORRECTED POWER FACTOR |  |  |  | 0.98
FACTOR FOR CORRECTION |  |  |  | 0.417
KVAR REQUIRED |  |  |  | 29.6667 | Kvar
SUGGESTED DESIGNED KVAR |  |  |  | 30 | Kvar
TOTAL AMP = 150AMP
REQUIRED BREAKER = 200 AMP
CABLE SIZE FOR 150 AMP = 95 Sqmm