## HIGH SIDE
NAME OF PROJECT: DHABA AT HYDERABAD
HVAC WORK (HIGH SIDE)
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
A | EQUIPMENTS |  |  | RATE |  | AMOUNT
1 | KITCHEN EXHAUST AIR SCRUBBER
Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications.
Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type SS Filters with aluminium mesh filters, Tungsten wire type type ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area, collection area should not be less than 6.0 sqmt, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state and entier unit should be CE Certified. all units shall have shall be equipped with Pulse width modulating (PWM) The system should be fitted with interlock switch for safety. The units should be BMS compatible for Feedback information on Run,Wash and Fault,dry contact point. The system should allow connection to a fan section to achieve velocity between 2.5 - 3.8 m/s across the air cleaner and should units should meet MERV 15 requirements even at velocity of 3.81 m/s (750 FPM)
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
ESP Power Consumption : Not more than 50W per cell.
Air Moving Capacities are as follows:
| 3000 CFM | No. | 1
2 | FAN COIL UNITS
Supplying, installing, testing and commissioning of horizontal powder coated Medium Static Chilled Water Fan Coil Units, blow thru type, Noscomplete with 3/4 rows deep chilled water coil, one or more centrifugal fans, aluminum/synthetic cleanable pre-filters,Digital thermostat with necessary control and power wiring with PVC conduit etc. type , primary inside pan SS-304 & secondary condensate drain pans outside of GI duly insulated, casing, coil, piping connections through copper pipes, condensate drain connection, All fan coil units shall be suitable for 220±6% volts, 50 cycles single phase power supply. All fan coils shall be with factory fitted with complete valve station, 2 way PIBC chilled water valve along with On -off type 220/230 volt AC actuator , brass made Y strainer type ball valve, brass ball valve.All valves shall be of minimum PN-16 pressure rating Quoted rates shall be inclusive of the cost of valve's thermal insulation (CFC & HCFC free) as specified for chilled water piping thermal insulation, 2 way PIBC Motorized Valves provided with spring return function in chilled water lines at Nosfan coil unit. The valves shall be suitable for suitable pipe sizes. 2 way PIBC control valve chilled water valve will be of PN16 rating complete with motor 220/230 volt AC of actuator of suitable torque.The valve should be IEC 534 compliant , have 20 mm stroke All shall be supplied as per tender specifications and data sheet. Fan coil unit shall be of following arrangement and refrigeration capacity.Control wiring from thermosets to FCU motor & PICV valve unto 20 Mtr. length shall be inclusive. 3C x 1.5 Sq.mm.Power cable of 3 mtr.length with 3 pin plug top from unit motor to the nearest power socket shall be included in the scope of supply.All supporting GI hangers, ,MS angles, channels nut , bolts, washers etc. necessary for unit installation shall be inclusive in the cost. Unit should supply with necessary Corded Remote Controller.
| 2.5 TR ( 1000 cfm) | Nos. | 1
TOTAL
GRAND TOTAL (SUPPLY + INSTALLATION)

## LOW SIDE
NAME OF PROJECT: DHABA AT HYDERABAD
HVAC WORK(LOW SIDE)
S.NO. | ITEM DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
A | EQUIPMENTS
(FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS)
1 | Supply, Fabrication, installation and testing of factory fabricated sheet metal ducts with sleeve joints and supports complete with the approved shop drawings and as required by the specifications and hanging of the ducts to be done by thread wire on metal cushion with gripple support.
| 18 G sheet | sq.m | 30
| 20G sheet | sq.m | 5
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 80
| 26G sheet | sq.m | 5
2 | Supplying and erecting GI sheet of fabricated at site and mentioned guage to be used for fabrication of ducting complete with neoprene rubber garkets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required:
| 18 G sheet | sq.m | 5
| 20G sheet | sq.m | 5
| 22G sheet | sq.m | 5
| 24G sheet | sq.m | 5
3 | THERMAL INSULATION FOR KITCHEN DUCTS
SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degreeC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade.
| 80 mm Thick | sq.m | 30
4 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Supply air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | SQMT | 2.5
5 | Supplying & fixing of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Volume control damper shall be provided at the junction of each branch duct with main duct. Dampers shall be 2 gauge heavier than the gauge of large duct but should not be less than 20 gauge, and shall be rigid in construction so as not to flutter with the passage of air. | SQMT | 1.5
6 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction square / round shape supply air diffusers with removable core & anti smudge ring & volume control dampers as per approved drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | Nos. | 1.5
7 | Supply, installation, testing and balancing of Powder coated extruded aluminium construction. Square / round shape return air diffusers with removable core, antismudge ring & without volume control damper as per specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 1.5
8 | Supply, fabrication, installation and testing the flexible connections constructed of fire resistance flexible double canvas sleeve as per the approved shop drawings. | Nos. | 2
9 | Supply, installation, testing and balancing of powder coated Extruded Aluminium Return air Grilles without volume control dampers in accordance with the approved shop drawings and specifications. (Minimum Chargable area would be 0.1 Sqm Per Pc) | sq.m | 4
10 | Supply, installation and testing of Acoustic lining with Open cell nitrile rubber with in supply and return air ducts of specified thickness as per the specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining as perthe specifications:
| 15 mm thick | sq.m | 10
11 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber(Class“O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
| 19mm thick | sq.m | 115
12 | Supplying, installing and testing of UPVC pipe ( heavy duty) with 6 mm thick nitrile rubber insulation with protective coating on condensing water piping and fitting like bends, elbow, tee and union, etc. as per the approved shop drawings and specifications.
| 25mm Dia | Rmt | 8
13 | Supply ,Installation ,Testing and commissioning of ERW heavy duty C Class MS pipes as per IS-1239 upto 6" dia. and as per IS-3589 above 6" dia. cut to required lengths and installed with all welded joints, complete with necessary pipe hot dip galvanized MS supports, GI hangers with rubber lined universal clamps and hangers , fittings like bends, elbows, tees, reducers, matching flanges, neoprene 6 mm thick gaskets, hot dipped galvanized nut & blots & washers ,PUF gutti with U clamp, socket and fittings for instruments and sensors connections etc. ERW pipes shall be with two coats of Zinc Chromate paint for anti-rust including all fittings like valves, flanges and unions, etc. Note : Pipe Measurement are in Pair (Supply + Return) . Quoted rates shall be inclusive of the cost of piping Insulation of Class O rated thermal insulations with one sided factory laminated glass clothed Nitrile Rubber insulation with density 45-60 kg/m3 with covered with two coats of UL Listed lag coating (Low VOC) Anti-fungal, Anti-microbial & vapour barrier for line item sealed with acrylic based food grade sealant.
| 25 mm dia MS Pipe with 25 mm thick Insulation | Rmt | 30
14 | Providing and fixing in position following ball valves
14.1 | 25 mm dia valves | Nos. | 4
15 | Providing and fixing in position the following ball valves with Y-strainer (PN 16).
15.1 | 25 mm dia valves | Nos. | 1
16 | Supplying, installation, testing and commissioning of Auto air vents.
16.1 | 25 mm dia pipes | Nos. | 1
17 | Supply, installation, testing and commissioning of THERMOSTAT for cooling. The thermostat shall be electronic room temperature controller with digital display & fan speed control, capable of providing individual space temperature control for cooling application. The controller shall produce a dual output to cooling coils in response to load change in rooms. The controller shall be designed to modulate two control devices such as 2 way motorized valves for chilled water duty . (minimum of 5 Deg F dead band ) | No. | 1
18 | Supply, installation, testing and commissioning of Electronic Self Balancing Valve pressure independent with independent type dynamic balancing valve for AHUs with integrated 2 way modulating control valves in a single body. The actuator shall be capable of accepting 2-10 VDC / 4-20 mA electric signal and shall provide similar transduced feedback output signal to control system for flow measurement. The minimum close off pressure actuator must be 1.5 times shut off head of pump 5 bars whichever is maximum. The valves shall be suitable for following pipe sizes:
18.1 | 25 mm dia | No. | 1
19 | Supply, Installation, Testing and Commissioning of BMS compatible ultrasonic BTU Meter complete with flanged type water flow meter (pressure drop across water meter not exceeding 0.1 bar at the specified nominal flow rate), temperature sensors, LCD display panel, inbuilt Lithium battery backup with minimum six years life. The units shall be capable to calculate and store maximum values, display flow rates and temperature difference across supply and return. The quoted price shall be inclusive of necessary wiring, conduiting between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box. The size of the BTU meter is as under:
19.1 | 25 mm dia BTU Meter | No. | 1
20 | Supply, installation, testing and commissioning of air curtain of 3 feet width having air throw velocity of 16 to 21 m/sec, with dual speed, Al chassis with CRC Plates, low noise level up to 56 to 59 dB suitable for door height upto 9 feet, working on 1ph, 230 V, 50Hz, A.C. supply. | Nos. | 2
GRAND TOTAL

## MAKE LIST
NAME OF PROJECT: DHABA AT HYDERABAD
HVAC APPROVED MAKES LIST
Sr. No. | Details of Materials / Equipment | Manufacturer’s Name
1 | Air Distribution Ducting (Site Febricated) | Sail / Nippon / OR Equivalent Approved
2 | Grilles / Diffusers / Jet Nozzles | Ravistar / Cosmos / Carryaire/ Airflow /Tristar/ Mapro Eq Approved
3 | Aero-Foil Dampers | Carryaire / Ravistar OR Equivalent Approved
4 | Fresh Air Louvers/Assembly | Ravistar/ OR Equivalent Approved
5 | Smoke / Fire Damper | Cosmos /Air Master / Caryaire / Dynacraft / Air Product / Ravistar/Tristar
6 | Flexible Duct Connectors | Klimatech,
7 | Anchor Fastener | Hilti
8 | Thermal Insulation on Kitchen Duct | UP Twiga, Owens Corning, Supreme
9 | Dry Scrubber | Rydaire / Trion / Halton
10 | Fan coil unit | Zeco/ Edgetech / Carrier/ Blue star / Waves
11 | M.S. Pipe upto 200 MM Dia. | AST / Jindal Hissar / Prakash Surya /Tata Steel
12 | UPVC Drain Piping | Prince / Supreme
13 | Filters | Dyna / Thermadyne / Spectrum / AAF OR Equivalent Approved
14 | Cushy Foot Mounts | Resistoflex/ OR Equivalent Approved
15 | Duct Thermal & Acoustic Insulation | Thermobreak / Supreme/ ARMACELL
16 | Closed Cell Nitrile Rubber along with adhesive | Armaflex / K-flex/ ARMACELL
17 | Motors | Siemens / HAVELL/ ABB / Bharat Bijlee / Marathon
18 | Cables | Polycab / Finolex / Hawells
19 | Switchgears- MCB’s, MCCB’s etc. | Legrand / Indo-Asian / Siemens
20 | Factory Made Duct | Alpha duct / Rollastar / Zeco / Nutech
21 | Ball valve | Honeywell/Zoloto/Emerald /Advance Valve /Navtech (Castle
22 | Auto Air Vent Valve | RB / Rapid Control
23 | PIBCV for FCU | Belimo / Danfoss / Honeywell / Schneider / Siemens
24 | Room Thermostat | Danfoss / Honeywell / Schneider / Siemens
25 | BTU Meter | Johnson Control / Honeywell / Kamstrup / Landis Gyr