## SUMMARY
Doc No. | B00B01-TFS-H_GN-DOM-02-BOQ-1201-RE
BIAL DOMESTIC LOUNGE - PHASE II
KITCHEN VENTILATION BOQ SUMMARY
Sr.No | Description | Total Amount
1 | VENTILATION SYSTEM | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
| TOTAL WITHOUT TAX | #REF!
CGST @
SGST @
Other taxes if applicable
| TOTAL WITH TAX | #REF!

## Kitchen Ventilation BOQ
BIAL DAY HOTEL
KITCHEN VENTILATION BOQ
Sr.No | Description | Unit | Qty | Rate | Total Amount
Note:
Prices shall be based on supply, installation, testing & commissioning (SITC) at site including all taxes, duties, transportation & insurance etc.
1 | VENTILATION SYSTEM
1.1 | KITCHEN EXHAUST AIR FAN
SITC of SISW Centrifugal Blower, Belt / Direct Drive, Statically & Dynamically Balanced, Backward Curved Impeller fan, Dunlop Anti- Vibration Pads etc. Motor should be outside stream with TEFC squirrel cage, weather protection shield, IP 55 rating with Class F Insulation, suitable for 3phase, 415volts, 50hz power supply. Sound level should be 60dB @ 3mtr distance. Fan should be painted with 2 coat of zinc chromate primer and 2 coats Epoxy paint. The quote shall include with MS frame, starter panel along with its required cable. Supplied with Dunlop Anti- Vibration Pads & Canvass Connection. (Vendor to crosscheck static pressure calculation).
a | 5000 CFM, 60mm Static (Class F) | No | 1 |  | 0
1.2 | INDUSTRIAL GRADE ELECTROSTATIC AIR CLEANER
SITC of Dry scrubber – Electrostatic Air cleaner with starter panel as per specifications, suitable for following capacities, including electrical starter panel . The Air filtration efficiency should be between 90 to 95% & units shall be staked one above other or side by side as per site requirement, if vendor will propose multiple units.
Finishing - Power coated, Dark Blue
Operating voltage - 220 Vac+/-10%, 50 Hz (Single phase)
Features - Short circuit, arc protection and auto restore power supply, BMS (Building Management System) terminals provided, Auto power cut-off when door is opened, Indicator LEDs for normal or wash indicator, Set of Terminals for remote LED normal or wash indicator
Efficiency - Upto 95%, meets NIOSH 5026 Oil Mist Test
Particle Size - Collects particles as small as 0.01 microns
Motor - Sealead ball bearings UL, single phase.
Cell - Ionizing voltage - 12 KVdc
Collector voltage - 6 KVdc
One cell comprising of 9 ionizing wires and 25 collection plates
Controls - Auto cut-off when door is opened. Indicator lights for fault, normal or wash function.
Pre-filter - Aluminium mesh, washable Dry contact for BMS.
a | 5000 CFM | No | 1
1.4 | FRAMEWORK FOR FANS
Supply, Fabrication and Installation of MS frame using channels/angle iron sections as required for mounting of ventilation fans & scrubber in areas shown in the layout. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be got approved from the Architects/ Structural Engineers prior to commencement of fabrication.
a | Exhaust Fan - 5000CFM | Lot | 1
b | Dry Scrubber - 5000 CFM | Lot | 1
Note:
a. | Fan outlet velocity - 1600 FPM
b. | All cabinet fans should have plenum section.
c. | Fresh air fan if any,should to have 6mm thick synthetic media washable filter with framework.
d. | Contractor shall submit static pressure calculation for all above units to Client/Consultant.
e. | Any change in motor HP or coil selection shall be made at no extra cost to client.
f. | Fan efficiency shall be minimum 75%
g. | The cost shall be included liftting & shifting of each equipment / material with all necesaary arrnagement. Also, it shall be included the cost of scaffloding required for Installation of such material / equipment.