## TechItemDoc
ItemCode | Item Name | UOM | Qty | Unit Price | Remarks
2 | Fire Alarm and PA SYSTEM-Supplying, installation, testing and commissioning of micro processor based intelligent addressable main fire alarm panel, central processing unit with the following loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5 % V, 50 hz), 48 hrs back-up with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog/digital voice evacuation system (which is part of the schedule of work under SH: PA System) and shall be complete with all accessories . The panel shall be compatible for IBMS system with open protocol BACnet/ Modbus over IP complete as per specifications.Ten Loop Panel. | Each | 1
3 | Supplying, installation, testing & commissioning of central graphical fire alarm management system to centrally monitor and operate the fire alarm system complete as required. | Each | 1
4 | Supplying, installation, testing & commissioning of repeater panel wih 320 character/ Touch screen LCD display with inbuilt reset, acknowledge and silence switches complete as required. | Each | 1
5 | Supplying, installation, testing & commissioning of intelligent analog addressable photothermal detector complete with mounting base complete as required. | Each | 8
6 | Supplying, installation, testing & commisssioning of intelligent addressable programmable sounder complete as required. | Each | 2
7 | Supplying, installation, testing & commissioning of fault isolator complete with base as required. | Each | 2
8 | Supplying, installation, testing & commissioning of addressable fire control or monitoring module complete as required. | Each | 2
9 | Supplying, installation, testing & commissioning of intelligent addressable duct detector including suitable Photo detector complete with base as required. | Each | 1
10 | Supplying, installation, testing & commissioning of addressable manual call point complete as required. | Each | 2
11 | Supplying, installation, testing & commissioning of addressable horn cum strobe complete as required. | Each | 2
12 | Supplying, installation, testing & commissioning of fire fighter telephone handset complete as required. | Each | 1
13 | Supplying, installation, testing & commissioning of fire fighter phone jack complete as required. Note: Fire survival cable for detectors considered. note: Conduit and wiring for MCP and Fireman telephone considered in SH: Wiring | Each | 30
14 | PA SYSTEM Supplying, installation, testing & commissioning of 1.5/3 W metal box ceiling/wall speakers complete as required.( 1.5 watt in corridors , 3 watt in basement) | Each | 8
15 | Supplying, installation, testing & commissioning of digital audio amplifier 75 Watt, 25V rms operating at 240 Volt AC Supply complete as required. | Each | 1
16 | Supplying and drawing of cable Fire Retardant PVC insulated copper conductor cable in the existing surface / recessed steel conduit of following pairs, cores and size including connections and interconnections etc. as required. Speaker cable Single pair, 2-core, 1.5 sqmm | Meter | 25
17 | Speaker cable Two pair, 2-core, 1.5 sqmm | Meter | 25
18 | Safety items -Supply and fixing of fire extinguisher, ABC Type 6.00 kg. capacity (ISI Marked IS : 15683 & TAC approved) complete with initial charge and wall bracket, along with supply of all materials and labour for proper completion of work. | Each | 9
19 | Supply and fixing of C02 type fire extinguisher 4.5 kg. capacity (ISI Marked IS : 2878 & TAC approved) complete with initial charge and wall bracket, along with supply of all materials and labour for proper completion of work. | Each | 9
20 | Supply and fixing of fire bucket, round bottom made of G.I. sheet 9-11 litres capacity duly painted as per fire brigade design, supported on hanging bracket chained and locked, initially filled with fine river sand, water as per directions of Engineer-in-Charge. | Each | 2
21 | Supply and erection of canopy type M.S.Structure made out of 40mm medium class M.S. pipe (Class B), 25 x 25 x 3 mm angle iron frame work and 14 SWG GI Sheet. Structure shall be grouted in C.C. 1:2:4 foundation for hanging 4 Nos. 9 litre each fire fighting buckets including providing buckets with two coats of anticorrosive paints etc. complete as required. | Each | 2