## CIVIL & INTERIOR WORKS
BOQ OF WANCHAI OUTLET AT T-1 FOOD COURT
CIVIL & INTERIOR WORKS
Client Name:- WANCHAI
Address: - T-1 DELHI FOOD COURT
Proposed Date- 17-12-2024
Deal Close Date :
ESTIMATE FOR INTERIOR WORK
Nos | Description of Items | Unit | Quantites | Rate | Amount
CIVIL WORKING
1 | 150MM THK WALL - Providing and constructing walls using of siporex block in 150mm wall in superstructure above plinth level in cement mortar 1:4 (1 cement : 4 coarse sand) including joints finished flushed/ raked to 6mm depth a work proceeds including iron reinforcement (2 nos. 8 mm dia) at every fourth coarse complete,scafolding all complete at all heights. The same shall be completed as per the details are provided in drawings as directed by architect. | Sq. ft. | 1080
2 | WALL PLASTER- Providing & Laying 12-15mm thick plaster in cement mortar 1:4 (1 cement : 4 coarse sand) to ceiling, all types of RCC. work, brick work surfaces at all levels in line, level and plumb including smooth cement finish or roughening of surface to hold tiles and providing necessary grooves at junctions of walls and ceiling, door/window frames inclusive of racking the joints, roughing the RCC. surface, necessary curing scaffolding etc., completed as per details given in drawing or as directed by Architect. | Sq. ft. | 1611
3 | SIPOREX BLOCK FILLING 300mm - Providing & Filling light wt. Siporex bat coba to conceal drainage & plumbing lines for Grease trap of average thk of 300 mm thick with CM 1:4. The rates shall include for Top layer should be finished properly to receive flooring layer on it. The same shall be completed as per the details are provided in drawings or as directed by Architect. | Sq. ft. | 135
4 | PCC 50 MM - Providing & Laying PCC 1:3:6 of average thickness of 50mm of M 10 grade of concrete ( 1 cement, 3 coarse sand, 06 graded stone aggregate of 20 mm nominal size) completed as per the details are provided in drawings or as directed by Architect. | Sq. ft. | 540
5 | WATER PROOFING-MEMBRANE - Providing and laying water proofing treatment as per the DIAL instruction. | Sq. ft. | 890
TILE WORKING
6 | FLOOR KOTA STONE - Providing & laying 25 mm thk Kota stone flooring of size 22" x 22" with 40 mm avg thk of cement sand bedding of CM 1:4 jointed with neat cement slurry & paste including hole cutting etc all necessary cutting, rubbing, grinding and mirror polish completed as per detail are shown in drawing or as directed by the Architect. (Basic cost of Kota Rs.50/- per SqFt) | Sq. ft. | 550
7 | "SKIRTING IN KOTA STONE KITCHEN /BOH AREA" Providing & fixing of 20 mm thk. kota stone 4" high with 12 thk base plaster of cement mortar 1:4 and joined with white cement slurry mixed with pigment to match the colour of KOTA including necessary wastage ,cutting ,grinding & polishing completed as per details given in drawing/Architect instruction.( Basic Rate of Kota stone Rs 50/ sft ) | Sq. ft. | 130
8 | FOH WALLS TILE (HIGHLIGHTER WALL TILE) - Laying of tiles in position for wall highlighter tile pasted with letigrade 315 grade chemical and joint with the white cement mixed with pigment to match the shade of tiles. The tile to be laid as per the approved pattern. Completed as per the details given in drawing and by the architect instruction. | Sq. ft. | 380
9 | "INTERNAL WALLS ( BOH AREA ) white glazed tile make; Kajaria/Johnson" Providing & Fixing of 300 x 450 white glazed ceramic tiles in kitchen area and Servent area pasted with letigrade chemical 315 grade joined with white cement slurry mixed with pigment to match the shade of tile. The tile to be laid as per approved pattern. Completed as per design & details are provided or as directed by Architect. ( Base Rate Rs.50/- Sq.Ft.) | Sq. ft. | 850
CEILING WORKING
| FOH AREA CEILING :- Providing and fixing False ceiling made up of flexible ply and mdf sheet in arc shape over wooden frame inclusive of all hangers, fastners, members and other clips complete with mdf sheet fixed with proper line and level and finished with the PU paint as per architectural drawings. All inclusive of cuttings, providing and making openings for light fixtures. | Sq. ft. | 155
| GYPSUM CEILING - Seamless Gypsum ceiling with gyp board of 12.5mm fixed to the under side of the suspended grid formed of GI perimeter channel of size 20x27x30mm fixed along the wall by using wood screws & metal expansion raw plugs. The GI intermediate channel of size 45x15x0.90mm shall be fixed to the suspended strap hanger /GI ceiling angle at intervals not more than 1220mm.The suspended GI ceiling angle/strap hanger is to be connected with G.I soffit cleat of size 37x27x25 1.6mm & it should be fixed on the roof slab/ beam by using metal expansion fasteners of 12.5mm dia. to the length of 35mm with screw at top ends, including all drops, coves etc and taping & finishing. | Sq. ft. | 434
WOODEN WORKING
| FOH ENTRY (VISION PANEL DOOR)- Providing, making & fixing Flush door (35 mm thk) finished with 1mm thk.laminate on both sides having vision panel of size 3'-0"x 1'-6" at eye level, SS door handle & 8" high 1mm thick SS Kick plate flush with laminate completed as per design & details provided by Architect. Rate shall inclusive of all necessary hardware (i.e. lock,SS Door handle on both sides, hetich butt 100mm long SS heavy duty bearing hinges, latch or tower bolt, door stopper, Floor Spring, Door PVC buffer, door closer, 6mm thick clear glass, frosted film, SS Kick plate etc. ) with beading. Door size shall be 3'-0" X 8'-0". Make of hardware & Accesories : Ozone/ Dorma/ Equivalent. (Basic cost of laminate:1500/- sheet). | Nos. | 1
| FRONT COUNTER - Providing & fixing of front counter finishing with 3" fascia White corian on the top and on the front counter top perimeter. Facia to be in finish printed vinyl paste on mdf over 19mm thk ply to be completed as per details & design provided in drawing or as per Architect's instruction. And rates are all inclusive. Fire rated wooden plyboard counter to be finished with white laminate from inside and shelves should be fixed in every storage. Measured area to be height and width of the counter | Sq. ft. | 50
| POS COUNTER -POS counter with 19mm commercialy ply with approved 1mm thk white laminate & top will be White corian with wooden shelves and shutters in every compartment as per approved detailed drawing. Measured area to be back of the counter. | Sq. ft. | 160
| TV STANDS- MS frame 2” x 4” pipes 14 gauge of MS pipes hang from the ceiling finish with PU coating with 19mm thk ply wrap over the MS pipe finish with 1mm thk laminate with TV stand for hanging TV. | Sq. ft. | 36
| FOH AREA ENTRANCE DOOR- Providing and fixing entrance door finish with ACP sheet design(color to be choose by the architect) over the 19mm thk ply front glazing include all hardware as per the detail drawing and design or directed by the architect. | Sq. ft. | 14
| WINDOW WORKING IN FOH AREA - Providing and fixing sliding window finish with the 1mm thk laminate completed as per the design and detail provided by the architect. | Sq. ft. | 5
PAINT WORKING
| CEILING PAINT- 3 coats of premium emulsion paint of approved quality & shade by sand papering the surface, applying one coat of primer, prepare the surface with two coats of full putty, sand papering again, repeating a coat of primer, applying one coat of plastic paint, touching up with putty & applying two final roller coats of paint, to internal wall/ceilings masonry concrete surfaces incl. preparing the surface by cleaning scrapping, smooth filling crevices, scaffolding etc. Paint codes will be provided by the client. | Sq. ft. | 830
TOTAL
GRAND TOTAL
Please note: work will be execute at site as per items mention in boq
AVIRA INTERIORS

## HVAC
BOQ _HVAC
Sr. No. | Description | Make List | Qty. | Unit | REMARKS
A | CEILING SUSPENDENT HANDLING UNITS
1 | Supply, Installation, Testing and Commissioning of Double Skin Ceiling Suspendent Air Handling Direct Driven Unit, made out of modular panel of thickness 43 +/- 2 mm thick, with thermal break profile, with following section: | Make-ZECO
CSU frame work shall be Anodized Aluminum Section with thermal break profile & internal coving.
Mixing box with FAD and RAD with AL construction.
Filter section with Pre-filter (G4) + Fine-filter (F5) (Combination Filter)
Cooling Coil section with 4 row deep CHW type cooling coil .
Fan Section with DIDW type Fan.centrifugal forward curved fan.ceiling suspendent direct driven.
Supply air damper in AL construction.
1.1 | CSAHU No : 01 @30mmWC - 2400CFM |  | 1 | NOS
2 | Kitchen Scrubber (Dry Type)-With Fan Section (Floor Mounted)
| 4500 CFM DIDW Blower Capacity at 110 MM SP |  | 1 | Nos.
Make : Trion / Rydair
2.1 | Supply, Installation, Testing and Commissioning of Dry Type Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)
The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12.5 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
Power Consumption : Not more than 50W per cell.
with Variable frequency Drive (VFD)
2.2 | DIDW Blower
Make: Systemair / Kruger/ VTS
DIDW Blower, motor, V belt drive, A.V mounting, supports etc. as per Specifications & Drawings
2.3 | Casing
Make: Systemair / Kruger/ VTS
Factory fabricated Double Skin construction shall have 25 mm thick PUF injected Panels having density 42 Kg/Cum with 0.8 mm pre-plasticized /pre-coated Galvanised steel sheet outside & 0.8 mm plain Galvanised steel sheet inside and fixed on 30x30 mm hollow extruded aluminium section. Casing shall be appropriately house both Electrostatic Modules and Fan with Drive.
Note: The Dry Scrubber shall be a single unit with 1 x 25000 CFM Dry Scrubber and DIDW Blower
2.4 | Accessories
The cost shall include all accessories like Adjusting motor brackets,base,vee drive belt & pulleys, vibration isolators, internal frame works ,canvas connection, Inlet/Outlet flange connection etc
Suitable silencer shall be installed in the discharge side to limit the noise to 75 db.
3 | FACTORY FABRICATED DOUBLE SKIN AIR WASHER | Nos | 1
Supply, installation, testing and commissioning of factory fabricated Double Skinned Air-washer unit floor mounted type fabricated out of extruded aluminium section with 0.6mm pre-plasticized / pre-coated Galvanised steel sheet outside & 0.6 mm plain Galvanised steel sheet inside with blower, blower section and blower motor TEFC (IE-3) type suitable for operation on 415 volts ± 10%, 50 Hz ± 5% AC supply, belt drive package, wet section & tank shall be made of 18 G stainless steel. The Air-washer shall be complete with fill of depth 200 mm & face velocity across the fill shall be limited to 152 MPM. The Air-washer shall have an efficiency of 90% & shall be complete with water circulation pump -2 Nos.(1W+1S), GI B Class interconnecting piping,Aluminum viscous filters. makeup, quickfill and drain connections, Butterfly/Gate valves for Pumps, make up, drain & quickfill connections of Sump, 2 Nos. pumps of suitable capacity (1W +1 S), Y strainers and necessary fittings etc. Suitable PCC/RCC foundation with plaster, Antivibration arrangement of cushy foot mountings etc.in all respect shall be in contractor's scope.
The Air-washer shall have an efficiency of 90% & shall be complete with water circulation pump GI B Class interconnecting piping & valves Aluminum viscous filters, fire retardent double canvass connection etc. The airwasher panels shall be insulated with 23mm thick & 36 Kg/m³ density PU foam. The Airwasher shall conform to specication given in the tender & shall be of following capacity. Motor Kw is indicative only, actual as per requirement to be included during installation.
Duty: Kitchen Fresh Air
Air Qty : 3600 CFM
Static Pressure : 90 mm wg
4 | FRESH AIR UNITS
1 | Supply, Installation, Testing and Commissioning of Double Skin Fresh Air Unit, made out of modular panel of thickness 25 mm thick, with thermal break profile, with following section: | Make-ZECO
F.A.H frame work shall be Anodized Aluminum Section with thermal break profile & internal coving.
Fan Section with DIDW type Fan.centrifugal forward curved fan.ceiling suspendent direct driven.
Supply air damper in AL construction.
1.1 | F.A.U No : 01 @30mmWC - 1200 CFM |  | 1 | NOS
1.2 | Drain Piping
Supply, installation, testing and commissioning of PVC drain piping complete with fittings, 'U' traps, supports for below pipe size.
i | 32 NB / 25 NB |  | 20 | Rmtr.
Note :- Piping quantity will vary as per actual site condition.
B | LOW SIDE DUCTING
1 | DUCTING
| Supply, fabrication and erection of following gauges of G.S.S. ducting complete with elbows spliters, supports/suspenders bends, tees, vanes, double canvas connection of the equipment etc., all complete as required. | Sheet Makes : Tata, Jindal, SAIL, Ispat
GI Sheet Makes : Tata, Jindal, SAIL, Ispat
Make: Rola Star, Zeco & Ductofab
i | 24 G |  | 450 | Sqmt.
ii | 22 G |  | 270 | Sqmt.
Note :- Ducting Quantity will vary as per actual site condition.
2 | MS angle along with red oxide primer and paint along with welding, drill holes for Nut Bolt for Duct Jointing and support of ducts. |  | 1000 | Kg
Note :- Quantity will vary as per actual site condition.
3 | DUCTING INSULATION
| SITC of Glass Fibre Blanket Insulation material bonded with Thrmosetting Resin, with factory applied laminated aluminium foil of 22 micrns with fibre glass backing. Further, wire mesh along with 7 mil cloth shall be applied on above the insulation with proper adhersive. Nominal density : 48 Kg/CuM. Thermal conductivity, < 0.033 W/m.K at 24 degC. All Insuation material and adhesives shall be as per Class I for surface spread and in accordance with BS 476, & Class O for non-combustible grade. | UP Twiga, Owens Corning, Supreme
i | Makes : UP Twiga, Owens Corning, Supreme
ii | 80 -mm Thick |  | 600 | Sqmt.
Note :- Actual Quantity will vary as per actual site condition.
1 | Supply & Return diffuser from TOP.
Supply, installation, testing and commissioning of extruded aluminium supply and exhaust air grille with/without dampers duly powder coated as per specifications and drawings.
i | 600mm x 600mm |  | 14 | NOS.
2 | EXTRUDED ALUMINIUM CEILING GRILLES
Supply, Installation, Testing and Balancing of Powder coated aluminium grilles complete with removable inner core as per approved shop drawing and specifications. The area of grille can be of any geometrical shape (Square/rectangular/Linear). The grilles shall be with 15/30/45° deflections as per requirement. The Colour shall be decided and approved by client and architect.
Make: Cosmos, Air Master & System Air
| Square / Rectangular / Linear |  | 3 | Sq.mtr
4 | VOLUME CONTROL DAMPER
| G.I. Duct Volume Control Damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. With suitable ducts lever and guadrants for manual control of volume of air flow. |  | 1.5 | Sqmt
Note :- Minimum applicable charges are 0.2 sq.mtr. for any damper size.
| VCD for Exhaust Hoods |  | 1 | Sqmt
Providing and fixing of powder coated extruded aluminium exhaust air louvers/ fresh air louvers with bird screen and mounting arrangement as per specification and drawings.
| Fresh / Exhaust Air Louvers with VCD and Bird Screen |  | 1.5 | Sqmt
5 | Motorised Fire Dampers
Supply, installation, testing & commissioning of motorised fire & smoke damper (spring return type) of approved make of atleast 90 min fire rating as per UL555, made out of 16 ga GSS and suitable for duct mounting with a flange of25/40 mm and depth of 150 mm. and as per the specification & detail given earlier in the relevant section. The fire damper shall be complete with electrically operated actuator and modbus compatible control panel and a supervisory controller (suitable for interconnecting upto 99 controllers) complete with all interlocking control wiring. The fire dampers shall be located in the supply/return ducts, at all fire rated crossovers(shafts/walls etc.). The control panel shall recieve signal from affected floor fire panel and shall actuate the dampers of affected floor , one floor above and one floor below (NC to NO). All other Fire Dampers to remain NC only. The Signal to the controllers from Fire Panel to be provided by electrical agency and Controller looping/ interlocking and looping with supervisory controller shall be in the scope of HVAC Vendor.(Cabling price separately considered in Part C below)
| Fire Dampers |  | 1 | Sqm.
| Actuators for motorized dampers |  | 2 | Nos.
6 | CANVAS CONNECTION
Supply & fixing of flexible Canvas connections between mouth piece and initial piece of ducting. Flexible connections shall be fire resistant made of closely woven, double layer canvass / neoprene coated fibre glass.
a | CHW AHU |  | 1 | No.
b | Cabinet Exhaust Fan |  | 1 | No.
c | Cabinet Fresh Air Fan |  | 1 | No.
7 | ELECTRICAL WORKS
7.1 | Power Cable:
Supply, handling, laying effecting proper connections testing and commissioning of following sizes of 1.1 KV grade XLPE insulated FRLS Aluminium / Copper conductor cables laid over MS supports cable racks or fixing on walls including clamping the cable to supports in an approved manner as required complete with Copper earthing as specified for continuous earthing along with cable. All complete as required and as per final instruction as given by Owners/ Consultants and as per Technical specifications. Earthing shall be measured separately and shall be connected in two runs. Power to ELCB to be provided near each ODU by electrical contractor.
a | CU Armoured Cable for Suitable 2400 CFM AHU Fan, 3PH Fan |  | 5 | Rmt
b | CU XLPE Cable for 4500 CFM EX Fan, 3PH Fan with Industrial Top Plug |  | 5 | Rmt
c | CU XLPE Cable for 3600 CFM FA Fan, 3PH Fan with Industrial Top Plug |  | 5 | Rmt
c | CU XLPE Cable for dry Scrubber, 1PH with Industrial Top Plug |  | 5 | Rmt
d | 8 SWG GI Earthing |  | 10 | Rmt
7.2 | CABLE TERMINATION :
Supply & Making of Cable termination of armoured / unarmoured cables 1.1 KV grade including installation of cable glands, cable lugs (Aluminium for A2XFY & copper for 2XFY & YY Double compression type), heat shrinkable sleeves on long ends, crimping paste etc. The work includes testing & commissioning of cables, meggaring values & submitting reports of tests. (One set includes termination of all cores of one end only). All crimping tools & dies shall be arranged by contractor.
a | CU Armoured Cable for Suitable 2400 CFM AHU Fan, 3PH Fan |  | 2 | Nos.
b | CU XLPE Cable for 4500 CFM EX Fan, 3PH Fan with Industrial Top Plug |  | 2 | Nos.
c | CU XLPE Cable for 3600 CFM FA Fan, 3PH Fan with Industrial Top Plug |  | 2 | Nos.
7.3 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type of height 50mm along with necessary bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports.
a | 50mm x 50mm x 1.6mm Thick |  | 20 | Rmt
b | 100mm wide x 50mm x 1.6mm Thick |  | RO | Rmt
SUB-TOTAL
GRAND TOTAL
General Guidelines:
Ducting:
1) Ducting shall be in accordance with IS 655, Galvanised Iron sheet to be used for all ducting works. Thermal insulation on ducts shall be 19 mm thick. Closed cell Class “O” BS 476 Part 6-7 FM Approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/(M⋅K)) at 0°C for air conditioning ducting.
2) Thermal insulation on kitchen exhaust ducting shall be 80 mm thick Aluminium foil faced resin bonded fiber Glass wool of density not less than 48 kg/m3
3) Thermal Insulation on Fresh air, Supply Air and Return Air shall be 19mm thick closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C.
4) Appropriate number of trap doors shall be provided in kitchen exhaust ducting for oil/grease cleaning purpose.
5) Ducting installation with respect to fresh air intake, kitchen exhaust out from location up to louvers at façade shall be in the scope of concessioner including air washer, exhaust fan section dry scrubber etc.
6) Each and every kitchen exhaust hood should be equipped with UL listed, wet chemical based, mechanically operated, automatic fire suppression system. Separate drawing to be submitted for Hood suppression system.
7) Supporting of ducting to be done with using angle 50x 50 x 5mm and tie rod of size minimum 10 mm dia/ As per duct size.
8) Post completion of onsite work, concessionaire has to share testing and commissioning report with DIAL.
9) Integration with Fire alarm system, so that AHU get switched off in case of any fire incident.
10) For equipment placement structural details to be approved by structural consultant and same to be share with DIAL.
11) Trap door with proper access to be provided for filter and copper coil cleaning.
12) Kitchen ventilation shall comply to NFPA 96 guideline.
Chilled Water Piping:-
1. Chilled water piping shall be confirming to IS:1239 Part I class ‘C’ heavy and fitting shall be conforming to ASTM A-105,3000lbs socket weld end (up to 50mm) & 1S:1239 Part-II HEAVY/ASTM A-234 WPB, Gr.B butt weld fitting ( above 50nb pipe size)
2. Piping connection should be socket welded up to 50nb size and shall be butt weld above 50nb pipe size. Pipe flanges should be confirming to ASTM A-105 # 150 SORF and flange dimension should be in accordance with ASME/ANSI B 16.5 (150 SORF), fitting to fitting welding is not allowed. Nozzle connections/thredolets/weldolets are not allowed by puncturing the pipe. Only equal/unequal Tee’s shall be used for branch connection from header. Socket weld end Tee should be used for branch connection (up-to -50nb pipe size) w.r.t to pressure gauge/temperature gauge/Air vent/Drain point etc.
3. Post installation clearance by DIAL, CHW piping shall be tested @15kgf/cm2 hydrostatics pressure for 24hrs hold time and Testing should be witnessed to DIAL Team.
4. Thermal insulation on CHW and condensate drain piping line shall be 25mm thick. Closed cell antimicrobial Class “O” BS 476 and part 6 & 7 FM approved nitrile rubber elastomeric insulation thermal conductivity 0.033 watts per meter-kelvin (W/ (M⋅K)) at 0°C.
5. Condensate drain piping shall be complying to IS 4985 Class 3 UPVC pipe. Solvent cement complying with ASTM D2564 shall be used for joints.
6. For ceiling suspended chilled water pipe: Pipe should be hanged with tie rod of size minimum 10 mm dia.
7. Attached CHW P&ID drawing/sketch to be followed during onsite work.

## F.F
FIRE FIGHTING SYSTEM
1 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. (Make - SURYA PIPES/ JINDAL HISSAR/ TATA)
a) | 25 mm dia. | Mtr | 15
b) | 32 mm dia. | Mtr | 3
c) | 40 mm dia. | Mtr | 3
d) | 50 mm dia. | Mtr | 4
e) | 65 mm dia. | Mtr | RO
f) | 80 mm dia. | Mtr | RO
g) | 100 mm dia. | Mtr | RO
2 | Providing, fixing, testing and commissioning brass quartzoid sprinklers K-80 (UL-Underwriters Laboratories Listed) suitable for 175 psi(12 Bars) maximum working pressure and 7 psi(0.5 Bars) minimum operating pressure with 15 mm dia BSPT threaded opening complete in all respects. The type & temperature rating shall be as follows. (Make - SAFEX/ NEWAGE/ HD FIRE)
a) | Pendent Concealed Sprinklers Sprinkler (68°)- Quick response type | Each | 7
b) | Pendent Concealed Sprinklers Sprinkler (93°)- Quick response type | Each | RO
c) | Upright Sprinkler (68°)- Quick response type | Each | RO
3 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required. (Make - SAFEX/ NEWAGE/ HD FIRE)
a) | 900mm | Each | RO
b) | 1200mm | Each | 7
c) | 1500mm | Each | RO
d) | 2000mm | Each | RO
4 | Providing & Fixing Powder coated double plate rosette plate for pendent / side wall sprinkler where ever required. (Make - SAFEX/ NEWAGE/ HD FIRE) | Each | RO
5 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required :
a) | 50 mm dia | Each | 1
b) | 65 mm dia | Each | RO
6 | Providing and fixing 150mm installation control valve assembly with turbine type automatic alarm to be connected with control valve, drain valve, test valve and piping as per manufacturer‟s specifications complete in all respects. | Each | RO
7 | Providing, fixing, testing and commissioning of drain test assembly complete with pipe, drain valve, test valve, sight glass, union, tee, elbow etc. complete with bolts, nuts, gasket, washers etc. as per NBC | Each | 1
8 | Providing and fixing electrically operated flow indicating switches model system sensor in sprinkler branch line including tamper switch and accessories, complete with tap off socket arrangement as required with necessary junction box installed in accessible place including Wiring from switches to panel | Each | RO
5 | FIRE EXTINGUISHER
a) | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and walll suspension braket as required as per specifications. (Make - MINIMAX/ SAFEX/ KALPEX/ PADMINI) | Each | 2
c) | Supply, installation, testing and commissioning of 4kg K-Type (For Kitchen) Fire Extinguisher. Mild Steel Cylinders ISI marked fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and conforming to IS:15683 as required as per specifications. (Make - MINIMAX/ SAFEX/ KALPEX/ PADMINI) | Each | 2

## FAS
FAS
SL. No | Description | Unit | Qty
2 | Fire Alarm and PA SYSTEM-Supplying, installation, testing and commissioning of micro processor based intelligent addressable main fire alarm panel, central processing unit with the following loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5 % V, 50 hz), 48 hrs back-up with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog/digital voice evacuation system (which is part of the schedule of work under SH: PA System) and shall be complete with all accessories . The panel shall be compatible for IBMS system with open protocol BACnet/ Modbus over IP complete as per specifications.Ten Loop Panel. | Each | 1
3 | Supplying, installation, testing & commissioning of central graphical fire alarm management system to centrally monitor and operate the fire alarm system complete as required. | Each | 1
4 | Supplying, installation, testing & commissioning of repeater panel wih 320 character/ Touch screen LCD display with inbuilt reset, acknowledge and silence switches complete as required. | Each | 1
5 | Supplying, installation, testing & commissioning of intelligent analog addressable photothermal detector complete with mounting base complete as required. | Each | 8
6 | Supplying, installation, testing & commisssioning of intelligent addressable programmable sounder complete as required. | Each | 2
7 | Supplying, installation, testing & commissioning of fault isolator complete with base as required. | Each | 2
8 | Supplying, installation, testing & commissioning of addressable fire control or monitoring module complete as required. | Each | 2
9 | Supplying, installation, testing & commissioning of intelligent addressable duct detector including suitable Photo detector complete with base as required. | Each | 1
10 | Supplying, installation, testing & commissioning of addressable manual call point complete as required. | Each | 2
11 | Supplying, installation, testing & commissioning of addressable horn cum strobe complete as required. | Each | 2
12 | Supplying, installation, testing & commissioning of fire fighter telephone handset complete as required. | Each | 1
13 | Supplying, installation, testing & commissioning of fire fighter phone jack complete as required. Note: Fire survival cable for detectors considered. note: Conduit and wiring for MCP and Fireman telephone considered in SH: Wiring | Each | 30
14 | PA SYSTEM Supplying, installation, testing & commissioning of 1.5/3 W metal box ceiling/wall speakers complete as required.( 1.5 watt in corridors , 3 watt in basement) | Each | 8
15 | Supplying, installation, testing & commissioning of digital audio amplifier 75 Watt, 25V rms operating at 240 Volt AC Supply complete as required. | Each | 1
16 | Supplying and drawing of cable Fire Retardant PVC insulated copper conductor cable in the existing surface / recessed steel conduit of following pairs, cores and size including connections and interconnections etc. as required. Speaker cable Single pair, 2-core, 1.5 sqmm | Meter | 25
17 | Speaker cable Two pair, 2-core, 1.5 sqmm | Meter | 25
18 | Safety items -Supply and fixing of fire extinguisher, ABC Type 6.00 kg. capacity (ISI Marked IS : 15683 & TAC approved) complete with initial charge and wall bracket, along with supply of all materials and labour for proper completion of work. | Each | 9
19 | Supply and fixing of C02 type fire extinguisher 4.5 kg. capacity (ISI Marked IS : 2878 & TAC approved) complete with initial charge and wall bracket, along with supply of all materials and labour for proper completion of work. | Each | 9
20 | Supply and fixing of fire bucket, round bottom made of G.I. sheet 9-11 litres capacity duly painted as per fire brigade design, supported on hanging bracket chained and locked, initially filled with fine river sand, water as per directions of Engineer-in-Charge. | Each | 2
21 | Supply and erection of canopy type M.S.Structure made out of 40mm medium class M.S. pipe (Class B), 25 x 25 x 3 mm angle iron frame work and 14 SWG GI Sheet. Structure shall be grouted in C.C. 1:2:4 foundation for hanging 4 Nos. 9 litre each fire fighting buckets including providing buckets with two coats of anticorrosive paints etc. complete as required. | Each | 2

## PHE BOQ
WANCHAI-PHE BOQ |  |  |  | Rev: | R0
|  |  |  | Date: | 19.12.2024
Item No. | Description | Unit | Qty | Rate | Amount | Make
A | WATER SUPPLY PIPING
1 | CPVC Pipes conforming to ASTM D-2846, SDR-11 grade and CPVC solvent weld fittings like elbows, tees, couplars, brass threaded adaptors, insert ring etc. suitable for (domestic and flushing) cold applications rated, concealed piping within wall / floor including jointing with fittings using solvent cement, brass threaded end fittings for making connection to fixtures. The work shall also include chasing the walls with machine wherever required for concealed piping and making good the same after laying of pipes & necessary pressure testing Chasing finishing shall be done with 1:1 cement mixed mortar, restore the same original condition for internal and shaft piping, including necessary hot deep galvanised supports vertical / horizontal, as per direction of Site incharge direction. [The rate shall include supply of S.S.screws and nut bolts etc.chasing in walls done by machine] (For Domestic and Flushing water-Toilet internal) (Pipe shall be tested with 1.5 times working pressure as covered in specifications) |  |  |  |  | Astral / Ashirwad /supreme / Prince or Approved Equivalent
1.1 | 20 mm Dia | R.mt | 35 |  | 0
1.2 | 25 mm Dia | R.mt | 30 |  | 0
1.3 | 32mm Dia | R.mt | 6 |  | 0
1.4 | 40mm Dia | R.mt | 0 |  | 0
1.5 | 50mm Dia | R.mt | 0 |  | 0
2 | Copper pipes and tubes shall be hand tempered conforming to requirements of EN 1057 ( formerly BS 2871) Table X , half and the fittings shall confirm the EN-1254-I ( Formerly BS 864: part-02). The fittings shall be end feed capillary fittings within wall/ceiling / floor including cutting & chasing the wall/ floor, jointing, making connection to fixtures, equipment and piping with purposes made connectors, etc. including insulation of closed cell elastomeric nitrile rubber. thermal conductivity of elastometric nitrile rubber shall not exceed 0.038w/m deg K. The insultaion should have fire performance and thickness of nitrile rubber should be 9mm (for hot water piping)
2.1 | 20mm Dia | R.mt | 35
2.2 | 25mm Dia | R.mt | 15
2 | Providing & Fixing of forged brass lever operated Ball Valves (10Kg/Sq.cm). Valve shall have with unions. |  |  |  |  | Leader / Neta / Zolotto / or approved Equivalent
2.1 | 20mm Dia | Nos. | 4 |  | 0
2.2 | 25mm Dia | Nos. | 0 |  | 0
2.3 | 32mm Dia | Nos. | 1 |  | 0
2.4 | 40mm Dia | Nos. | 0 |  | 0
2.5 | 50mm Dia | Nos. | 0 |  | 0
3 | Providing ,fixing, testing and commissioning Electromagnetic flow meter-flow (12 GPM-0.76 LPS) including providing & fixing matching with required accessories 16Kgs/Sq.cm). - Contractor to check existing make and provide that. |  |  |  |  | ENH/Porsh Marshal or approved Equivalent
3.1 | 25 mm Dia incoming line | Nos. | 1 |  | 0
3.2 | 32 mm Dia incoming line | Nos. | 0 |  | 0
3.3 | 40 mm Dia incoming line | Nos. | 0 |  | 0
3.4 | 50 mm Dia incoming line | Nos. | 0 |  | 0
4 | Supply, installation,testing & commissioning of Storage Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories |  |  |  |  | AO Smith or Approved Equivalent
4.1 | 5 L Capacity- | Nos. | 0 |  | 0
4.2 | 20 L Capacity | Nos. | 1 |  | 0
4.3 | 35 L Capacity- For shower | Nos. | 0 |  | 0
5 | Supply, installation,testing & commissioning of Stiebel Type Electric Hot Water Generator of mentioned capacity, suitable for 3 KG/cm2 pressure, Wall Mounted / Floor standing type, with Auto Shut-off Thermostat, along with isoltion Valves, Air Release valve, SS flexible connections andall other std accessories (Optional in pantry) |  |  |  |  | Stiebel Entron or Approved Equivalent
5.1 | 3.5kw in pantry- optional | Nos. | 0 |  | 0
5.2 | 8kw | Nos. | 0 |  | 0
5.3 | 13kw-3ph- Subject to load permits | Nos. | 0 |  | 0
6 | RO PACKAGE PLANT-Supply , installations, testing and comminissioning of ECO SMART-100 | No | 0 |  | 0 | Make- Ion Exchange/ or equivalent
7 | Supply, Installation, Commissioning & Testing for Booster pump for Ro water supply WITH FLOW SWITCH GRAVITATIONAL FLOW (top to bottom flow) with both side Sensor operations- A) 3CUM PER HR. B) HEAD: 25M, C) PHASE: SINGLE PHASE, D) PROTECTION: IP55, E) MONOBLOCK TYPE, with sensors cabling & Control panel.(Pump shall be Auto fill stop and Auto empty start mechanisam) |  |  |  |  | Grundfoss /Kirloskar / Bharat Bijli / Agasti / or Approved Equivalent
7.1 | 0.75 HP | Nos. | 1 |  | 0
7.2 | 1.5 HP | Nos. | 0
8 | Supply, Installation of sintex loft mounted water tank of 50 Ltrs | Nos. | 0 |  | 0 | Sintex
9 | P/F water level Indicator on loft water tank by means of a transparent clear tube fixed along height of the water tank hence making water level visible | Nos. | 0 |  | 0
10 | Providing & Fixing Brass Non Return Vavles of ISI mark. Rates are for BRASS valves |  |  |  |  | Make – KITZ / ZOLOTO / AUDCO /or Approved Equivalent
12.1 | 20mm | Nos | 2
12.2 | 25mm | Nos | 2 |  | 0
12.3 | 40mm | Nos. | 0
11 | SITC of Eco smart RO-50 with all required accessories | Nos | 0 |  | 0 | Iron Exchange or Approved Equivalent
12 | SITC of standalone Ro -12 lit with all required accessories | Nos | 0 |  | 0 | Iron Exchange or Approved Equivalent
13 | SITC of ACO grease trap -model Lipumobil 0.8 -Capacity -48 lit ( 0.8 LPS) with all required accessories ( Order shall be placed as per space available below the counter) | Nos | 0 |  | 0 | Aco or Approved Equivalent
14 | SITC of ACO grease trap -model Lipumobil S -Capacity -32 lit ( 0.5 LPS) with all required accessories | Nos | 0 |  | 0 | Aco or Approved Equivalent
15 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 20 ( 34.3. lit) | Nos. | 1
16 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 14 ( 25.5. lit) | Nos. | 1
17 | Installalation , testing commissioning of S.S. Grease trap nurgreen Make -NGT 50 ( 72 lit) | Nos. | 1
A | SUB TOTAL OF A |  |  |  | 0
B | DRAINAGE
1 | UPVC-SWR pipes (working pressure 10kg/cm2) conforming to IS 13592/92 and IS 14735-type-B solvent posted ( for Dia above 50mm) and for ( Dia below 50mm) shall be as per IS 4985 and 7834 Class-05 (10 kg/cm2) including cutting the pipes to required lengths, laying in the position to required grade and level, jointing, supporting with PVC cleat,hot deep galvanised bracket supports,hot deep galvanised nut-bolts, anchor fastners, PVC coated U-clamp, testing and rectifying leakages for piping within vertical shafts / supported on wall / hung below slab etc. with all material & labor complete and as directed. [The Rate shall include supply and fixing of nesessary items] Vertical line bracket shall be fixed at every 0.8 mtr to 1.00 mtr.] |  |  |  |  | Supreme / Finolex / Prince / Oriplast / or Approved Equivalent
1.1 | 40mm Dia | R.mt | 0 |  | 0
1.2 | 50mm Dia | R.mt | 6 |  | 0
1.3 | 65mm Dia | R.mt | 0 |  | 0
1.4 | 75mm Dia | R.mt | 0 |  | 0
1.5 | 100 mm Dia | R.mt | 28 |  | 0
1.6 | 150 mm Dia | R.mt | 0 |  | 0
2 | Supply, Install PVC Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 1 |  | 0
3 | Supply, Install PVC Multi Floor Trap for the following pipes including making all approved quality Solvent cement joints with material & labour etc. all complete as per direction of the engineer-in-charge. | Nos. | 5 |  | 0
4 | Supply, Install PVC urinal Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0 |  | 0
5 | Supply, Install PVC P- Traps including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0 |  | 0
6 | Supply, Install PVC clean out plug including fixing with necessary consumables with Circular SS Grating with anti cockroach jali Suitable for 75mm Dia outlet | Nos. | 0 |  | 0
| SUB TOTAL OF B |  |  |  | 0
C | SANITARY AND C. P. FITTINGS & FIXTURES
Supply & installation, testing and commissioning of sanitary and C.P. fittings( Client /Architect to select the model no as required and provide fixtures)
1.1 | EWC with seat cover | Nos | 0 |  | 0
1.2 | Concealed flush tank | Nos | 0 |  | 0
1.3 | Concealed flush valve | Nos | 0 |  | 0
1.4 | Health Faucet | Nos | 0 |  | 0
1.5 | 2 Way Bib-Cock with connection for Health Faucet | Nos | 0 |  | 0
1.6 | Bided | Nos | 0 |  | 0
1.7 | Under Counter Wash Basin including waste Coupling | Nos | 0 |  | 0
1.8 | Wash Basin Cock | Nos | 0 |  | 0
1.9 | shower and mixer | Nos | 0 |  | 0
1.1 | Jet Spray | Nos | 0 |  | 0
1.11 | Bath Tub including waste Coupling and nessessary connections | Nos | 0 |  | 0
1.12 | Under Counter Sink including waste Coupling | Nos | 3 |  | 0
1.13 | Sink Pillar Cock - Jaquar continental series | Nos | 3 |  | 0
1.14 | Bottle Trap for WHB/ sink and urinal with all connecting pipes | Nos | 0 |  | 0
1.15 | Angle Cock with PVC pipe connection upto WHB/sink/Geyser connection Jaquar continental series | Nos | 4 |  | 0
1.16 | Urinal | Nos | 0 |  | 0
1.17 | Auto Flush Valve & Sensor with connecting piping & spreader for urinal(DC) | Nos | 0 |  | 0
0
| SUB TOTAL -C-SANITARY AND C. P. FITTINGS & FIXTURES ( ONLY INSTALLATIONS) |  |  |  | 0
D | S.S. GRATING
Supply , installations/ testing and commissioning of S.S.Gratings
1 | Supply installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS perforated tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling) Entire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 3
2 | Supply & installation of S.S Grating size, 600mm x 300mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. (100 mm Dia S.S 304 grade finish unions reducers/coupling or 75mm Dia S.S 304 grade finish unions reducers/coupling or 50mm Dia S.S 304 grade finish unions reducers/coupling)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 0
3 | Supply & installation of S.S Grating size, 600mm x 600mm, in 16 swg 25mm x25mm Square Pipe around the Frame and 20mmX 20mm Square pipe in center of frame with SS Closed tray (304 SWR). Complete as per architectural detail drawing & Site Engineer's instruction. ( at hook up point)ntire Chamber will be made in 16 SWG SS 304 , Testing of Chamber as per DIAL Guideline | Nos. | 1
SUB TOTAL -D-S.S. GRATING INSTALLATION
GRAND - TOTAL A , B, C AND D
NOTES :
1. Taxes and duties shall be Extra as actual
Water Supply: General comments
Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.
Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter and water meter power supply should be on UPS source.
General Guidelines (Water Supply) .
Water supply pipe laying for FOH, should be laid in niche with openable cover, for BOH it could be exposed.
Supply Line installation check & leakage testing to be done, before connection with DIAL tapping point.
Specification for Supply pipe- 1) CPVC ASTM D-2846 SDR-11 Class-1, CPVC solvent ASTM F-493 for normal water
For Hot water: Copper pipe EN 1057 with thermal insulation. Thermal insulation shall be conforming to BS 476 Part 6&7 FM approved, Fittings BN-1254-1,
Pipe installation in walls (except washroom and shower room) shall be through niches with openable SS cover.
All materials/items to be used at site are subjected to prior inspection and approval from DIAL Engg. Data sheet with respect to all material need to be submitted for prior approval.
Test certificate with respect to all material need to be submitted prior to installation during MIR Process.
Make– Astral/Supreme for Pipe and Fittings.
· All pipes should be installed freely from ceiling void area. Water Supply piping from floor is not allowed. Piping drops from ceiling inside BOH areas are recommended to be exposed on walls/partitions. In FOH areas, piping drops from ceiling can be installed through niche in walls with openable S.S. covers. Needs to be mentioned in drawing.
· Existing Water Meter should be easily accessible.
· Hydro-testing of pipe to be done at a pressure of 15Kgf/cm² for 24 hrs and get it inspected from DIAL- Engg
Water meter /Isolation valve shall have adequate space and access for maintenance of valve & water meter and taking reading of water meter. Kindly share section drawing of same and water meter power supply should be on UPS source.
Data Sheet, material inspection & Catalogue needs to be submitted for prior approval from DIAL-Engg.
Kindly note our water meter is digital which will be integrated with the BMS, so whatever cable will be installed during the shifting of water meter, will concessionaire scope.
General Guidelines (Drainage) . To be followed during execution work
Grease trap Make shall be as per TDM and selection and backup calculation shall be as per TDM and have adequate space for opening of top cover for maintenance. Kindly share the details.
Cleanout provisioning for maintenance and cleaning purpose to be provided.
Water proofing for wet & Dry to be done as per TDM/Airport guideline.
Pipe laying to be done within trench, and trench flooring should have openable cover.
Power to be provided for existing Digital Water meter.
Drain Line testing to be done, before connection with DIAL tapping point.
Required JB/Openable trench cover/Grating/Floor trap/IC to be provided.
Specification for Drain Pipe- uPVC IS:4985 Class 5 & IS:7834 Class 5 for fittings, uPVC solvent- ASTM D-2564, Makes – Astral/Supreme for Pipe and Fittings.
Pipe installation in raised flooring should be through trench with openable cover.
Each and every drain should go through Grease Traps. Only Condensate drain of HVAC Units are allowed to be conned without Grease Trap. Calculations w.r.t drain flow rate with grease capacity need to be submitted w.r.t selection of Grease Traps Capacities. Only S.S. Grease Traps are allowed. Data Sheet & Catalogue needs to be submitted for prior approval from DIAL-Engg.
Size of IC should not be less than 600MMx600MM. S.S. grating with dia 5mm holes should be permanently welded inside IC at discharge end.
Y- Connections to be provided instead of Tee in uPVC waste pipe.
Note-
Before execution, all Material inspection to be done along with TDS & required test certificates.
Installation check to be done, before closing of ceiling & Flooring
Post completion of onsite work, As Built Drawing to be submitted.
DIAL Shared Guideline to be followed

## ELE SUM
SUMMARY OF COST OF INTERIOR & EXTERNAL-ELECTRICAL & ELV WORK - SKYHIGH BIRYANI
SR. | DESCRIPTION | TENDER AMOUNT (Rs.)
NO. | OF ITEM |  | MAT. | INST. | TOTAL
1 | PANELS / DBs | Rs. | 0 | 0 | 0
2 | CABLES : | Rs. | 0 | 0 | 0
3 | POINT WIRING : | Rs. | 0 | 0 | 0
4 | RACEWAYS, CABLE TRAYS & JUNCTION BOX | Rs. | 0 | 0 | 0
5 | LIGHT FIXTURES INSTALLATION | Rs. | 0 | 0 | 0
6 | EARTHING : | Rs. | 0 | 0 | 0
7 | Miscellaneous Item | Rs. | 0 | 0 | 0
8 | DATA DISTRIBUTION | Rs. | 0 | 0 | 0
9 | SUPPLY & INSTALLATION OF SAFETY ITEMS | Rs. | 0 | 0 | 0
10 | UPS/ INVERTER System: | Rs. | 0 | 0 | 0
11 | CCTV | Rs. | 0 | 0 | 0
12 | PA SYSTEM | Rs. | 0 | 0 | 0
13 | #REF! | Rs. | #REF! | #REF! | #REF!
| TOTAL | Rs. | 0 | 0 | 0
NOTE:- | GST Extra
Exclusions:
1. Passive data network devices and active networking components are excluded.
2. Epabx & Telephone instruments are excluded.
3. SERVER is excluded.
4. Light Fixture- Supply Excluded.

## Electrical
BILL OF QUANTITY FOR ELECTRICAL WORK FOR WANCHAI
TENDER BOQ. R0
SR. | DESCRIPTION OF ITEM | UNIT | QTY | UNIT RATE (Rs.) |  | AMOUNT (Rs.)
NO. |  |  |  | MAT. | INST. | MAT. | INST. | TOTAL
1 | PANELS / DBs
Supply and Installation of main LT panel,genarally conforming to IS 8623/IS-13947/IEC-439 front operated, dead back floor mounted , totally enclosed, compartmentalised, vermin proof,indoor, non-drawout type,power panel, fabricated out of 2/1.6mm thick CRCA sheets, fully powder coated after seven tank treatment, having gasketed & hinged cover on each cubicle with insulated door knob, incorporating horizontal and vertical copper busbars complete with all internal wiring, danger sign board, earth-bus and lugs, cable chamber, busbar chamber,aluminium anodized name plates etc.as required, including 2 nos. of 6" dia instrument cooling fan with switch and ventilation louvres with wire mesh,housing below mentioned switchgears / meters. 9W fitting with CFL lamp, switch shall be provided in each vertical section,:(Panel should conform to Form- 3b of IEC- 439) (GA drawing of the panel to be got approved from the Consultant before taking up fabrication and all panels to be factory inspected before despatch)
Notes: 1. All MCCBs shall have rotary handle
2. All MCCBs shall have phase spreader assembly on
both Line & Load ends.
3. All MCCB shall have Minimum Ics=Icu
4. Incomer shall have auxilliary ON/OFF & TRIP status contacts and the same shall be wired up
electronic trip setting to Metering Compartment)
5. The panel shall conform to Form-3b as per IEC-439
6. All MCCB to be of Schneider/ABB make
7. All MCCB to be current limiting type, LSIG
8. Incomer MCCB to be shunt trip facility
7. With DOL Starter 2.2KW & 1.5KW for air washer & exhaust fan
8. With VFD for 2.2KW & 1.5KW for air washer & exhaust fan make Selec
9.Please provide CO2,FM200/HFC-227ea gas based automatic tube detection & suppression system needs to be installed in Electrical Panel
Refer: SLD
1.1.1 | MAIN PANEL | Set | 1 |  |  | 0 | 0 | 0
1.2 | Suply and installation of Four -Tier, Multi-Way, TPN,
Distribution Board for Lighting & Power distribution, surface
mounted on wall, sheet metal fabricated,powder coated,
having dust-proof and vermin 'proof, gasketed and hinged
acrylic door with all internals such as DIN rails, neutral-link,
interconnected wiring complete with earthing lugs housing
switchgears: (IP-43 with Metal Door) Refer: SLD & DB Schedule
(Make: Legrand-Ekinoxe /Schneider)
1.2.1 | KITCHEN DB 1 (KPDB-12WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.2 | KITCHEN DB 2 (BARDB-8WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.3 | LPDB 1 (12WAY TPN) | Set | 1 |  |  | 0 | 0 | 0
1.2.4 | UPS OUTPUT | Set | 1 |  |  | 0 | 0 | 0
1.2.4 | UPSDB (16WAY SPN) | Set | 1 |  |  | 0 | 0 | 0
1.4 | S & I of 32A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 0 |  |  | 0 | 0 | 0
1.5 | S & I of 16A, TPN, MCB type Isolator + 415 V, Industrial Power socket in powder coated metal box for supplying power to AC equipment etc. IP65 | Nos | 8 |  |  | 0 | 0 | 0
1.6 | S & I of 40A, TP, MCB + 415 V, in powder coated sheet metal box for terminating UPS to UPS DB etc. | Nos | 0 |  |  | 0 | 0 | 0
1.7 | S & I of 20A,SP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
1.8 | S & I of 16A,SP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Set | RO |  |  | 0 | 0 | 0
1.9 | S & I of 6/10A,SP ELCB + 220 V, Industrial Power socket in powder coated metal box for supplying power to Kitchen equipment etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
1.1 | S & I of 32A,TP ELMCB 300mA, Metal clad,Power socket in powder coated metal box for supplying power to AC etc. IP65 | Nos | RO |  |  | 0 | 0 | 0
| Sub Total of 1.0 |  |  |  |  | 0 | 0 | 0
2 | CABLES :
2.1 | Supply and laying, effecting proper connections, testing & commissioning of the following sizes of 1.1 KV XLPE armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to supports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire. Necessary Markers shall be provided at the intervals as per the specifications.
2.1.1 | 3.5C x 120 Sq.mm. AL Cable- MAIN PANEL | R.M | RO |  |  | 0 | 0 | 0
2.1.2 | 3.5C x 95 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.3 | 3.5C x 70 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.4 | 3.5C x 50 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.5 | 3.5C x 35 Sq.mm. AL Cable | R.M | 80 |  |  | 0 | 0 | 0
2.1.6 | 3.5C x 25 Sq.mm. AL Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.7 | 4C x 16 Sq.mm. CU Cable - KPDB1 & KPDB2, ELECTRIC HOT PLATE | R.M | 80 |  |  | 0 | 0 | 0
2.1.8 | 4C x 10 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.9 | 4C x 6 Sq.mm. CU Cable - KITCHEN EXHUAST & FRESH AIR | R.M | 20 |  |  | 0 | 0 | 0
2.1.10 | 4C x 4 Sq.mm. CU Cable - AHU | R.M | 20 |  |  | 0 | 0 | 0
2.1.11 | 4C x 2.5 Sq.mm. CU XLPE Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.12 | 4C x 2.5 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.13 | 3C x 16 Sq.mm. CU able | R.M | RO |  |  | 0 | 0 | 0
2.1.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | R.M | 50 |  |  | 0 | 0 | 0
2.1.15 | 3C X 4sq.mm CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.16 | 3C x 2.5 Sq.mm. CU Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.17 | 3C X 4sq.mm CU PVC Cable | R.M | RO |  |  | 0 | 0 | 0
2.1.18 | 3C X 1.5sq.mm CU PVC Cable | R.M | 20 |  |  | 0 | 0 | 0
2.1.19 | 1C x 70 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.1.20 | 1C x 4 Sq.mm, Copper, Flexible, Bunched together | Mtr. | RO |  |  | 0 | 0 | 0
2.1.21 | 2C X 2.5sq.mm CU Cable | R.M | 25 |  |  |  |  | 0
2.1.22 | 5C X 2.5sq.mm CU Cable - LCS | R.M | 25 |  |  |  |  | 0
2.2 | CABLE TERMINATION
Making cable and terminations including brass single compression glands and crimping type copper lugs for cable sizes mentioned below for aluminium or copper.
2.2.1 | 3.5C x 120 Sq.mm. AL Cable- MAIN PANEL | Nos. | RO |  |  | 0 | 0 | 0
2.2.2 | 3.5C x 95 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.3 | 3.5C x 70 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.4 | 3.5C x 50 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.5 | 3.5C x 35 Sq.mm. AL Cable | Nos. | 2 |  |  | 0 | 0 | 0
2.2.6 | 3.5C x 25 Sq.mm. AL Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.7 | 4C x 16 Sq.mm. CU Cable - KPDB1 & KPDB2, ELECTRIC HOT PLATE | Nos. | 8 |  |  | 0 | 0 | 0
2.2.8 | 4C x 10 Sq.mm. CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.9 | 4C x 6 Sq.mm. CU Cable - KITCHEN EXHUAST & FRESH AIR | Nos. | 2 |  |  | 0 | 0 | 0
2.2.10 | 4C x 4 Sq.mm. CU Cable - AHU | Nos. | 6 |  |  | 0 | 0 | 0
2.2.11 | 4C x 2.5 Sq.mm. CU XLPE Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.12 | 4C x 2.5 Sq.mm. CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.13 | 3C x 16 Sq.mm. CU able | Nos. | RO |  |  | 0 | 0 | 0
2.2.14 | 3C X 6sq.mm CU Cable - UPS, UPS DB | Nos. | 7 |  |  | 0 | 0 | 0
2.2.15 | 3C X 4sq.mm CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.16 | 3C x 2.5 Sq.mm. CU Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.17 | 3C X 4sq.mm CU PVC Cable | Nos. | RO |  |  | 0 | 0 | 0
2.2.18 | 3C X 1.5sq.mm CU PVC Cable | Nos. | 2 |  |  | 0 | 0 | 0
2.2.19 | 1C x 70 Sq.mm, Copper, Flexible, Bunched together | Nos. | RO |  |  | 0 | 0 | 0
2.2.20 | 1C x 4 Sq.mm, Copper, Flexible, Bunched together | Nos. | RO |  |  | 0 | 0 | 0
2.2.21 | 2C X 2.5sq.mm CU Cable | Nos. | 8 |  |  | 0 | 0 | 0
2.2.22 | 5C X 2.5sq.mm CU Cable - LCS | Nos. | 8 |  |  | 0 | 0 | 0
| Sub Total of 2 |  |  |  |  | 0 | 0 | 0
3 | POINT WIRING :
3.1 | LIGHT POINT
Sub mains / Pre-Primary wiring i.e. from DB to room switch board shall be carried out for Pre-primary point using 2.5 sqmm copper stranded. All lighting fixture, wiring shall be carried out for primary point using 2.5 sqmm copper stranded & for secondary wiring 1.5sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduits" (including flexible conduits for drops to light fittings)". Individual junction / inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.
also including insulated green color copper earth wire for each circuit and providing modular grid plate type switches,sockets etc. as required. Each light point to be terminated using 5A connector or 5A two pin female socket (for cove lighting) as directed at site. Each circuit feeding not more than 12-8 points/800 watts as per following configuration:(LDBs located at two locations as shown) (The Switch Socket cost shall be paid separately.)
From distribution board to switch board will be termed as Pre-primary point, average wiring length for Pre-primary point to be considered as 15 metres. From switch board to first light fitting and switch board to switch board will be termed as primary point, average wiring length for primary point to be considered as 6 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 4 metres. Light point wiring shall be included submains wiring from D.B. to room switch board.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.1.1 | Pre-Primary point (sub mains point) | Nos | RO |  |  | 0 | 0 | 0
3.1.2 | Total points | Nos | 40 |  |  | 0 | 0 | 0
3.2 | LIGHT POINT- for AUTOMATION
All lighting fixture, wiring shall be carried out for primary point using 1.5 sqmm copper stranded & for secondary wiring 1.5sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduits" & 1 pair 1.5sqmm jacketed cable in Separate Conduit (including flexible conduits for drops to light fittings)". Individual junction / inspection boxes shall be provided for each lighting fitting for the purpose of looping from fitting to fitting.
From DB to first light fitting/driver will be termed as primary point, average wiring length for primary point to be considered as 20 metres and First fitting to subsequent fitting on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 5 metres. Light point wiring shall be included submains wiring from D.B. to room lights/Driver.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.2.1 | Primary point | Nos | RO |  |  | 0 | 0 | 0
3.2.2 | Secondary Point | Nos | RO |  |  | 0 | 0 | 0
3.3 | Power Point (Utility)
Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 2.5 sqmm copper stranded. Secondary wiring 2.5sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduit". Individual junction/inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.
From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 15 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 6 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.3.1 | Primary point | Mtr. |  |  |  | 0 | 0 | 0
3.3.2 | Secondary Point | Nos |  |  |  | 0 | 0 | 0
3.4 | Power Point (Kitchen & FOH)
Primary wiring i.e. from DB to first power point shall be carried out for primary point using 3R x 4 sqmm copper stranded. & Also used 3R x 2.5sqmm copper stranded. Secondary wiring 4 sqmm copper stranded conductor 660/1100V grade PVC FRLS insulated wire in "GI Conduits". Individual junction/inspection boxes shall be provided for each power point to loop from power point to a power point. Only 4 points looped in one circuit) From DB to First Socket.
From distribution board to first power point will be termed as primary point, average wiring length for primary point to be considered as 22 metres. First power point to subsequent power point on the same circuit shall be termed as secondary point, average wiring length for secondary point to be considered as 1 metres. Power point wiring shall be included wiring from D.B. to room indivisual power point.
Note: Length may vary as per actual site condition. Vendor shall be crossverify before bidding.
3.4.1 | total points | Nos | 36 |  |  | 0 | 0 | 0
3.5 | S & I of GI conduits including all accessories, clamps, spacers, bends, tee, cross etc. as required at site for miscellaneous use in following sizes:
3.5.1 | 20mm dia | Mtr | RO |  |  | 0 | 0 | 0
3.5.2 | 25mm dia | Mtr |  |  |  | 0 | 0 | 0
3.6 | S & I of flexible GI conduits including all accessories, clamps, spacers, end adopters (Glands) etc. as required at site in following sizes:
3.6.1 | 20mm dia | Mtr | RO |  |  | 0 | 0 | 0
3.6.2 | 25mm dia (COMMON) | Mtr |  |  |  | 0 | 0 | 0
3.7 | Supply, Installation testing and commission of 240V-AC, wiring devices and its accessories such as modular shuttered type switch socket outlets with modular front plate, on Suitable MS box, G.I. back box and all required accessories etc. Supply & Installation scope includes all civil works related to this job such as chiselling , making good with concrete and plaster, supply of fixing screw / wall plugs and other necessary hardware, marking identification numbers of circuits & interconnections of the switch /sockets as per standard drawing, complete as per site requirement. Switches and sockets may be individual or combined with bigger lighting switchboards, contractor to refer drawings to understand exact scope of work. LEGRAND
3.7.1 | 6A SWITCH & SOCKET(UTILITY POINT) | Nos. | 5 |  |  | 0 | 0 | 0
3.7.2 | POS COUNTER | Nos. | 1 |  |  | 0 | 0 | 0
3.7.3 | 5A PLUG POINT | Nos. | RO |  |  | 0 | 0 | 0
3.7.4 | 5/15A POWER PLUG POINT(MODULAR SWITCH & SOCKET) | Nos. | 10 |  |  | 0 | 0 | 0
3.7.5 | 20/32A METAL CLAD WITH 20A SP MCB & PLUG TOP | Nos. | 4 |  |  | 0 | 0 | 0
3.7.22 | 5 Pin Industrial 16A Socket (3 PHASE) | Nos. | 4 |  |  | 0 | 0 | 0
3.7.24 | DATA POINT | Nos. | 1 |  |  | 0 | 0 | 0
| Sub Total of 3.0 |  |  |  |  | 0 | 0 | 0
4 | RACEWAYS, CABLE TRAYS & JUNCTION BOX
4.1 | S & I of GI trunking same as above but of size 100mm x 40mm x1.6 mm for power cables.(Electrical Room) | Mtr | RO |  |  | 0 | 0 | 0
(PROFAB/ASIAN/Approved equivalent)
4.2 | S & I of trunking same as above but of size 85mm x 38mm x1.6 mm thick for power/data cables. | Mtr | RO |  |  | 0 | 0 | 0
4.3 | S & I of trunking same as above but of size 65mm x 38mm x1.6 mm thick for power/data cables. | Mtr | RO |  |  | 0 | 0 | 0
(PROFAB/ASIAN/Approved equivalent)
4.4 | S & I of 1 Run x 25mm dia, GI Conduit in Floor. | Mtr | 6 |  |  | 0 | 0 | 0
4.5 | S & I of floor junction boxes similar to above but size 350mm x 350mm x 60 mm | Nos | RO |  |  | 0 | 0 | 0
4.6 | S & I of floor junction boxes similar to above but size 250mm x 250mm x 60 mm | Nos | RO |  |  | 0 | 0 | 0
4.7 | S & I of floor junction boxes similar to above but size 150mm x 150mm x 60 mm | Nos |  |  |  | 0 | 0 | 0
4.8 | S & I of GI Pregalvanizd Perforated type Cable Tay
of following sizes suspended from ceiling or fixed
vertically on wall/column as per route directed at site
including all necessary bends, tees, crosses and also
including all necessary supporting arrangement.
All supporting hardware including nuts, bolts etc.
shall be also of galvanised M.S. as approved
(PROFAB/INDIANA/ASIAN/approved equivalent)
4.8.1 | 100mm x 50mm x 1.6mm | Mtr |  |  |  | 0 | 0 | 0 | 1470
4.8.2 | 300mm x 50mm x 1.6mm | Mtr |  |  |  | 0 | 0 | 0 | 168
4.8.3 | 450mm x 50mm x 2.0mm | Mtr |  |  |  | 0 | 0 | 0 | 90 | 375
150
| Sub Total of 4.0 |  |  |  |  | 0 | 0 | 0 |  | 420
5 | LIGHT FIXTURES INSTALLATION | [8 empty] | 210
5.1 | Installation of lighting fixtures with lamps as per the details below including necessary hardware such as clamps, nuts, bolts, nails screws and suspension rods as required for fixing the fixtures in position as directed by architect / consultant at site.
5.1.1 | CEILING PANEL LIGHT | Nos | 20 |  |  | 0 | 0 | 0
5.1.2 | HANGING LIGHT | Nos | 5 |  |  | 0 | 0 | 0
5.1.3 | CYLINDRICAL LIGHT | Nos | 20 |  |  | 0 | 0 | 0
| Sub Total of 5.0 |  |  |  |  | 0 | 0 | 0
6 | EARTHING :
6.1 | S & I of earth pit comprising of specially designed SEE/Ashlok brand Earth Electrode system 3.00 meter long including necessary materials like side fill compound etc. as required with standard brick masonary chamber with hinged cover and watering arrangement model SEE-60/C with SFC-20/Equivalent ASHLOK MODEL T39 HD (50MM DIA. 3 MTR) | Nos | 2 |  |  | 0 | 0 | 0
6.2 | S & I of copper /GI earthing wires/strips in following sizes
6.3 | 8 SWG GI bare wire | Mtr | 50 |  |  | 0 | 0 | 0
6.4 | 8 SWG CU bare wire | Mtr | 20 |  |  | 0 | 0 | 0
6.5 | 25mm x 3mm thick GI strip welded & painted green | Mtr | RO |  |  | 0 | 0 | 0
6.6 | 25mm x 6mm thick GI strip welded & painted green | Mtr | 40 |  |  | 0 | 0 | 0
6.7 | S & I of isolated/dedicated earthing / grounding system for computers etc.using insulated green-yellow copper earthing wire laid/fixed bare on wall/ceiling from separately made earth pit to the equipment in following sizes The rate shall include termination also.
6.7.1 | 6 Sqmm copper, yellow-green/green insulation | Mtr | 10 |  |  | 0 | 0 | 0
6.8 | S & I of Main bus for isolated earth comprising of 300mm x 25 mm x 3mm thick Tinned copper bar fixed on insulated support and having 10 nos of holes and nut bolts studs for clamping the earth leads,all contained in MS/PVC box and having transparent acrylic cover as approved by the consultant | Nos | 1 |  |  | 0 | 0 | 0
| Sub Total of 6.0 |  |  |  |  | 0 | 0 | 0
7 | Miscellaneous Item
7.1 | Supply & Install. Of RG 6 TV Cable in 25mm PVCConduit | Mtr. | 45 |  |  | 0 | 0 | 0
7.2 | Supply & Laying of RG11 use for Main Cable TV | Mtr. | 45 |  |  | 0 | 0 | 0
7.3 | Install. Of Digital Screen - Only Installation | Nos. | 7 |  |  | 0 | 0 | 0
| Sub Total of 7.0 |  |  |  |  | 0 | 0 | 0
8 | DATA DISTRIBUTION
Supply, Installation, termination & testing of data system:
8.1 | Main SERVER / ROUTER | Nos. | RO |  |  | 0 | 0 | 0
8.2 | SMART GIGABIT SWITCH 16 PORTS | Nos. | 1 |  |  | 0 | 0 | 0
8.3 | Loaded PATCH PANEL for 16Port | Nos. | 1 |  |  | 0 | 0 | 0
8.4 | LIU switch with Accessories. (Optional : if Fibre Optic Cable terminated) | Job | 1 |  |  | 0 | 0 | 0
8.5 | Supply & Installation of I/O DATA Outlet (RJ-45) | Nos. | 2 |  |  | 0 | 0 | 0
8.6 | S & I of Installation of Wi-Fi ceiling mounted Access Point, managed by controller software | Nos. | RO |  |  | 0 | 0 | 0
8.7 | Supply, installation, termination & testing of all Terminations using Fluke Cable Analyser DTX 1800 for all CAT 6 Information Outlet including Information outlet | Lot | RO |  |  | 0 | 0 | 0
8.8 | CABLES:
8.8.1 | S&I Optical Fiber Cable with 12 fibers, with core dia. 50/125 µm (OM3), suitable for 1GBps Ethernet distance at 850 nm of wavelength, | Mtr. | RO |  |  | 0 | 0 | 0
8.8.2 | S&I Optical Fiber Cable with 6 fibers, with core dia. 50/125 µm (OM3), suitable for 1GBps Ethernet distance at 850 nm of wavelength, | Mtr. | RO |  |  | 0 | 0 | 0
8.8.3 | Supply & providing of CAT 6 UTP cables in the laid raceways/Conduits including terminations | Mtr. | 16.8 |  |  | 0 | 0 | 0
8.8.4 | Patch cord (2 mtr-user end) | Each | 2 |  |  | 0 | 0 | 0
8.9 | Supply, Installation, Testing & Commissioning of Velcro Ties ( 22 Mtrs = 1 Roll) | Roll | 1 |  |  | 0 | 0 | 0
8.10. | Supply, Installation, Testing & Commissioning of Cable Ties 200mm ( 100 Nos. Pkt) | Pkt. | 1 |  |  | 0 | 0 | 0
8.11 | Project Management including Freight & Forwarding, Cable Bunching, Printed Numbering, tube type Ferruling both sides, Face plate, Patch panel & patch cords both sides, Documentation etc.. | Job | 1 |  |  | 0 | 0 | 0
8.12 | Supplying and fixing 6U Rack Aluminium Frame - 600x600mm with 4 x FAN, Dual Split perforated Door at Front and Back Side, 2 x Vertical Cable Basket, 2 x 12 socket 5/15A PDU with MCB, side Panels of 2 nos and Heavy Duty Castors with break, 19" Reduced Channel - Loop Type (DATA+CCTV) | Job | 0 |  |  | 0 | 0 | 0
8.13 | Supply & installation of GI Conduits with junction boxes, reducer etc. complete concealed/surface mounting as required.
| Sub Total of 8.0 |  |  |  |  | 0 | 0 | 0
9 | SUPPLY & INSTALLATION OF SAFETY ITEMS
9.1 | Sand buckets with stand (set of 3 buckets) | Sets | RO |  |  | 0 | 0 | 0
9.2 | Caution boards (11kV) of standard Size | Nos | RO |  |  | 0 | 0 | 0
9.3 | Caution boards (415V) of std. Size | Nos | 1 |  |  | 0 | 0 | 0
9.4 | Rubber mat at panel room 12mm thk. 1mtr. Wide | Mtrs | 1 |  |  | 0 | 0 | 0
9.5 | Shock treatment chart as per electricity board | Nos | 1 |  |  | 0 | 0 | 0
9.6 | First aid box with standard items | Nos | RO |  |  | 0 | 0 | 0
9.7 | 11 KV rating rubber hand gloves | Sets | RO |  |  | 0 | 0 | 0
9.8 | The contractor to submit all the AS BUILT DRAWINGS after the completion of the project for Electrical & ELV Services executed at site. | Part of Tender |  |  |  | 0 | 0 | 0
| Sub Total of 9.0 |  |  |  |  | 0 | 0 | 0
10 | UPS/ INVERTER System:
10.1 | Supply, Installation, testing and commissioning of 3 KVA UPS System Single Phase I/C & Single Phase O/G complete with 30 Minutes Battery Back-up the required accessories as specified in the drawings & the specifications. Make: Emerson/APC/Consul Neowatt/Vivtar Electronics | set | 1 |  |  | 0 | 0 | 0
| Sub Total of 10 |  |  |  |  | 0 | 0 | 0
11 | CCTV
11.1 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Dome + Night vision. Camera Make: CP-PLUS | Nos. | 0 |  |  | 0 | 0 | 0
11.2 | Supply & Installation of 2 Megapixel IR-20Mtr. IP Indoor Bullet Camera+ Night vision. Camera Make: CP-PLUS | Nos. | RO |  |  | 0 | 0 | 0
11.3 | Supply & Installation of 2 Megapixel IR-30Mtr. IP Outdoor Bullet Camera + Night vision. Camera Make: CP-PLUS | Nos. | RO |  |  | 0 | 0 | 0
11.4 | Supply & Installation of 16 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | 0 |  |  | 0 | 0 | 0
11.5 | Supply & Installation of 24 Channel NVR with 4 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | RO |  |  | 0 | 0 | 0
11.6 | Supply & Installation of 16 Channel NVR with 2 Sata Hard Disk Slot (Make: Honeywell/CP PLUS) | Nos. | 0 |  |  | 0 | 0 | 0
11.7 | Supply & Installation of 16Port PoE Switch (Make: Systimax) | Nos. | 0 |  |  | 0 | 0 | 0
11.8 | 6 TB HDD Hard Disk | Nos. | 0 |  |  | 0 | 0 | 0
11.9 | Monitor/PC system | Nos. | 0 |  |  | 0 | 0 | 0
11.1 | Supply & Installation of 3+1 Cable for Camera with GU Couduit | Mtr. | 90 |  |  | 0 | 0 | 0
| Sub Total of 11 |  |  |  |  | 0 | 0 | 0
12 | PA SYSTEM
12.1 | Supply & Installation of 6W Ceiling Speaker with box | RM | RO |  |  | 0 | 0 | 0
12.2 | Control Unit (with volume and on/off switch) (Smooth stepless control, but the control shall be through dimmer switch, the make of which will be same as the make of light control switches) | Nos. | RO |  |  |  |  | 0
12.3 | Supply & Installation of 120W Booster Amplifier | Nos. | RO |  |  | 0 | 0 | 0
12.4 | Installation of 2 core 2.5 Sq.mm PVC insulated twisted copper conductor Speaker wires as required. | RM | RO |  |  | 0 | 0 | 0
| Sub Total of 12 |  |  |  |  | 0 | 0 | 0
General guideline for onsite electrical works:
1. DB have per phase RCBO protection.
2. Minimum wire size shall be 2.5 Sq. mm and power circuits wire size should be 4.0 sq.mm.
3. All equipment’s above 1 KW shall be provided with ELCB & shall run/operated through industrial type switch socket only.
4. Only GI conduit will be used.
5. Equipment protection devices and appropriate earthing as per approved load to be provided.
6. All DB and panel have dual earthing connection.
7. All internal wires / cables shall be FRLSH/FRLSZH.
8. Main distribution board will not be fixed on wooden material.
9. IT , Data and low voltage wires shall be drawn In Separate
10. Switch/ Sockets outlets will not be over loaded with multiple connection conduit and not with electrical
11. All lights shall be LED.
12. Provision of Emergency light should be there.
13. No combustive material are to be store under/closed the electrical switch board/distribution board/meter etc.
14. The concessioner should install suitable type & rated fire extinguisher near electrical panel.
15. Shutter type switch socket outlet on suitable MS box shall be used with proper earthing.
16. All electrical equipment shall be proper earthed and connected to main earthing with suitably sized earthing conductor.
17. Final approved Single line diagram sealed in a plastic folder shall be provided inside each electrical panel.
18. Load balancing to be done.
19. Power connection for Existing BTU meter & Water meter to be provided from concessionaire DB.
20. All electrical source to be enclosure with IP65 Device with louvered openable cabinet and all fire protection.
21. Panel GA drawing to be share with DIAL for approval.
22. Before installation, material inspection to be done.
23. Test certificate for installed electrical material to be submitted to DIAL .
24. If any changes due to site constraint, prior intimation to be provided to DIAL. Post approval only SLD to revised.
25.all SP MCB as ‘C’ characteristic.
In case, Incomer rating equal to or more than 200Amps: Automatic Tube Detection and Suppression System to be done
CO2,FM200/HFC-227ea gas based automatic tube detection & suppression system needs to be installed for Electrical Panel with Incomer rating equal to or more than 200Amps.
Drawing needs to be submitted for prior approval.
System sizing & design calculations also need to be incorporated in drawing.
Thanks & Regards